SOUTHERN POWER DISTRIBUTION COMPANY OF TELANGANA LIMITED

HYDERABAD

DISTRIBUTION COMPANY OF TELANGANA  LTD

LIGHTING   UP   YOUR   LIVES

SOUTHERN

POWER

BID No.Chief General Manager/Master Plan /GH/TSSPDCL:  06-A/2022-23.

NAME OF THE WORK: CONSTRUCTION OF COMPOUND WALL FOR NEWLY ALLOTTED LAND OF UPPAL BHAGAYAT PHASE-II LAYOUT, FOR PROPOSED OF NEW 33/11KV SUB-STATION IN HABSIGUDA CIRCLE, MASTER PLAN RR CIRCLE OF MASTER PLAN ZONE (RESERVED UNDER WADDERA/SAGARA CATEGORY).

PART-I

(TECHNICAL BID)

&

PART-II

(PRICE BID)

Chief General Manager

Master Plan, TSSPDCL,

Mint Compound, Gr. Hyderabad.

SOUTHERN POWER DISTRIBUTION COMPANY OF TELANGANA LIMITED

Master Plan Zonal office, Mint Compound, Hyderabad – 500063.

# e- Tendering Bid Notice (web Site)n hand

Bids are invited through e-Tendering from eligible Bidders for Construction of Compound Wall for newly allotted land of Uppal Bhagayat Phase-II layout, for proposed of new 33/11KV Sub-Station in Habsiguda Circle, Master Plan RR Circle of Master plan Zone (Reserved under Waddera/Sagara category) .

The Bid document will be made available from 13.03.2023 at 15.00 Hrs and the last date for uploading of Bid is dt.20.03.2023by 15.00Hrs.

.

Further details of Bid Specification may be browsed from Web site of TSSPDCL www.tssouthernpower.com & https://tender.telangana.gov.in

Chief General Manager/Master Plan

TSSPDCL, Hyderabad.

CONTENTS

- INVITATION FOR BIDS (IFB)

- SECTION – 1: INSTRUCTIONS TO BIDDERS (ITB)

- SECTION – 2 : QUALIFICATION REQUIREMENT

- SECTION – 3: CONTRACT DATA

- SECTION – 4: GENERAL CONDITIONS OF CONTRACT

- SECTION – 5: TECHNICAL SPECIFICATIONS

- SECTION – 6: QUALITY ASSURANCE PLAN

8.	SECTION – 7: SCHEDULE OF QUANTITIES AND PRICES

9.	SECTION – 8: SAFETY MEASURES

10.	SECTION – 9: FORM OF BID, QUALIFICATION

INFORMATION, PERFORMANCE SECURITY,     BANK GUARANTEE AND LETTER OF ACCEPTANCE

NOTE:

1.    “Payment terms, Performance Bank Guarantee, Taxes and Duties” should be in line with the Terms and Conditions of the Bid specification. If any Bidder does not meet any one of the conditions, such Bid will not be considered.

Hence the Bidder shall submit the Bid in line with the Terms and Conditions of the Bid specification only.

2	The Bidders shall check the website www.tssouthernpower.com & https://tender.telangana.gov.in for amendments, if any, up to one day prior to the date of Bid opening. The amendments shall be binding on the Bidders.

Chief General Manager 	                    				           	                                                Master Plan, TSSPDCL

Mint Compound, Gr. Hyderabad

INVITATION FOR BIDS

SOUTHERN POWER DISTRIBUTION COMPANY OF TELANGANA LIMITED

MINT COMPOUND HYDERABAD – 500 063

E-mail:-cgmmphyd@gmail.com

NOTICE for inviting the Bids for Construction of Compound Wall for newly allotted land of Uppal Bhagayat Phase-II layout, for proposed of new 33/11KV Sub-Station in Habsiguda Circle, Master Plan RR Circle of Master plan Zone (Reserved under Waddera/Sagara category).

BID No. Chief General Manager/Master Plan/GH/TSSPDCL: 06-A/2022-23

The Southern Power Distribution Company of Telangana Limited (TSSPDCL) is looking forward for Construction of Compound Wall for newly allotted land of Uppal Bhagayat Phase-II layout, for proposed of new 33/11KV Sub-Station in Habsiguda Circle, Master Plan RR Circle of Master plan Zone (Reserved under Waddera/Sagara category)

In order to take up the above works, the TSSPDCL invites Bids from the eligible bidders.

The various span of the Bidding process will be as per the following schedule:

| BID No.Chief General Manager/Master Plan/GH/TSSPDCL: 06-A/2022-23 |  |  |  |
| --- | --- | --- | --- |
| Sl. No. | Description of Item | Date | Time |
|  | Construction of Compound Wall for newly allotted land of Uppal Bhagayat Phase-II layout, for proposed of new 33/11KV Sub-Station in Habsiguda Circle, Master Plan RR Circle of Master plan Zone (Reserved under Waddera/Sagara category) |  |  |
| 1. | Schedule start date & time for downloading Bid document on e-procurement web site | 13.03.2023 | 15.00Hrs |
| 2. | Bid Submission closing date & time on line | 20.03.2023 | 15.00Hrs |
| 3. | Last date & time for submission of hard copies along with DD’s or BGs. | 21.03.2023 | 12.00Hrs |
| 4. | Technical Bid opening date & time | 21.03.2023 | 15.00 Hrs |
| 5. | Date & time of Price Bid opening | 23.03.2023 | 15.00 Hrs |

All the interested bidders may visit https://tender.telangana.gov.in to view and download the Bid documents free-of-cost. Those who are interested to submit Bids shall have to register in the above-mentioned site and must obtain Digital Certificates.  The details and procedure for obtaining digital certificate are mentioned in the website or contact the helpdesk of the site.

TSSPDCL

BID No.Chief General Manager/Master Plan/GH/TSSPDCL: 06-A/2022-23

Annexure

| Notice Inviting Bid Details |  |  |
| --- | --- | --- |
| Sl. No. | Description |  |
| 1 | Department Name | TSSPDCL |
| 2 | Office | Chief General Manager / MasterPlan / TSSPDCL. |
| 3 | Bid Number | BID No. Chief General Manager/Master Plan/GH/TSSPDCL:06-A/2022-23 |
| 4 | Name of the Work | Construction of Compound Wall for newly allotted land of Uppal Bhagayat Phase-II layout, for proposed of new 33/11KV Sub-Station in Habsiguda Circle, Master Plan RR Circle of Master plan Zone (Reserved under Waddera/Sagara category) |
| 5 | Work completion Schedule | 4 months |
| 6 | Type of Bid | e-tender |
| 7 | Bid Category | Open tender |
| 8 | Bid Validity | 90 Days |
| 9 | Bid Security (INR) | Bidders shall furnish an amount of Rs.49,838/- (2% of the Bid value incl. of 18% GST ) for BGs or DD or online Payment. |
| 10 | Bid Security Payable to | In the form of Online/Demand Draft in favor of Accounts officer, Master Plan, TSSPDCL, Gr. Hyderabad from any scheduled or nationalized bank or online payment through e- procurement platform. Alternatively, the Bidders may furnish a B.G (Nationalized /Scheduled bank acceptable to the Employer) in original in favour of Chief General Manager/ Master Plan/TSSPDCL, Hyd. as per the proforma attached and it should be valid for 6 months from the uploading starting date of the Bid. Fax/photocopies of the Bid security will not be accepted and will be rejected. The fact of having enclosed bid security by DD/BG along with the Bid should be clearly super scribed on the Bid envelope. |
| 11 | Transaction Fee | Transaction Fee: All the participating Bidders who submit the bids have to pay an amount @ 0.03% of their final Bid value online with a cap of Rs.10, 000/- for quoted value of work up to Rs.50 Cores and Rs. 25000/- if the quoted value of work is above Rs.50 crores & service tax applicable as levied by Govt. of India on transaction fee through online to M/s Vupadhi. Corpus Fund: Successful Bidder has to pay an amount of 0.04% on quoted value through demand draft in favour of Managing Director Vupadhi., Hyderabad towards corpus fund at the time of conclusion of agreement. Or as mentioned in the e-procurement platform |
| 12 | Transaction Fee Payable to | Vupadhi, Hydperabad. Or as mentioned in the e-procurement platform |
| 13 | Bid submission closing date & time (for uploading) | 20.03.2023at 15.00Hrs for uploading 21.03.2023 at 12.00 Hrs for Hard copies |
| 14 | Bid Submission | On line |
| 15 | Technical Bid opening date & time | 21.03.2023 at 15.00 Hrs |
|  | Price Bid opening date & time | 23.03.2023 at 15.00 Hrs |
| 16 | Place of Tender Opening | Office of the Chief General Manager / Master Plan / TSSPDCL/ Mint Compound, Gr.Hyderabad -500063. |
| 17 | Officer Inviting Bids/Contact Person | Chief General Manager / Master Plan / TSSPDCL/ Mint Compound, Gr. Hyderabad -500063. |
| 18 | Address | O/o the Chief General Manager / Master Plan / TSSPDCL / Mint Compound, Gr.Hyderabad -500063. |
|  | E-mail Id | cgmmphyd@gmail.com |
| 19 | Contact Details/Telephone, Fax | - |
| 20 | Procedure for Bid Submission | - Bids shall be submitted online on https://tender.telangana.gov.in platform. - The participating Bidders in the Bid should register themselves free of cost on e-procurement platform in the website https://tender.telangana.gov.in - Bidders can log-in to e-procurement platform in secure mode only by signing with the Digital certificates. - The Bidders who are desirous of participating in e-tendering shall submit their technical Bids, price Bids as per the standard formats available at the e-procurement platform. - The Bidders are requested to scan and upload the documents mentioned in clause 4.3 in of support of technical bids and any other documents as specified in the ITB. - The rates should be quoted in online only. |
|  |  | 7. For each uploaded document on line, the Bidder should provide the index of the file names and its contents invariably. |
|  |  | 8. The hard copies as mentioned in the checklist/ clause 4.3 and any other documents as specified in the ITB are to be attested by gazette officer and submitted as part of technical Bid. |
|  |  | 10. The attested hard copies are to be submitted on or before 21.03.2023, 12.00hrs otherwise the Bid will be treated as non-responsive. |
|  |  | 11. The Department shall not hold any risk on account of postal delay; similarly, if any of the certificates, documents, etc., furnished by the Bidder is found to be misleading/false/fabricated/bogus, the Bidder will be disqualified and blacklisted duly forfeiting the Bid security. 12. The department will not hold any risk and responsible regarding non-visibility of the scanned and uploaded documents. 13.Important Notice to Contractors, Suppliers Department users In the endeavor to bring total automation of processes e-Procurement, the Govt. has issued orders vide G.O.Ms.No.13 dated.5-07-2006 permitting integration of electronic Payment Gateway of ICICI/HDFC Banks with e-Procurement platform, which provides a facility to participating suppliers/contractors to electronically pay the transaction fee online using their credit cards. |
| 21 | Rights reserved with the Department | TSSPDCL reserves the right to accept or reject any or all the Bids received without assigning any reasons therefor. |
| 22 | General Terms and Conditions | As per Bid document. |

SECTION -1

INSTRUCTIONS TO BIDDERS (ITB)

| ### INSTRUCTIONS TO BIDDERS |  |  |  |
| --- | --- | --- | --- |
| TABLES OF CLAUSES |  |  |  |
| A. GENERAL |  | D. SUBMISSION OF BIDS |  |
| 1. Scope of Bid 2. Source of Funds 3. Eligible Bidders 4. Qualification of the Bidder 5. Cost of Bidding 6. Site Visit B. BIDDING DOCUMENTS 7. Content of Bidding Documents 8. Clarification of Bidding Documents 9. Amendment of Bidding documents C. PREPARATION OF BIDS 10. Language of the Bid 11. Documents Comprising the Bid 12. Bid Prices 13. Currencies of Bid and Payment 14. Bid Validity 15. Bid Security 16. Alternative Proposals by Bidders 17. Format and Signing of Bid |  | 18. Sealing and Marking of Bids 19. Deadline for Submission of Bids 20. Late Bids 21. Modification and Withdrawal of Bids E. BID OPENING AND EVALUATION 22. Bid Opening 23. Process to be Confidential 24. Clarification of Bids 25. Examination of Bids and Determination of Responsiveness 26. Correction of Errors 27. Evaluation and Comparison of Bids F. AWARD OF CONTRACT 28. Award Criteria 29. Employer’s Right to Accept any Bid and to Reject any or all Bids. 30. Notification of Award & Signing of Agreement 31. Performance Security 32. Mode of payment 33. Corrupt or Fraudulent Practices 34. Quality assurance plan |  |

A. GENERAL

- SCOPE OF BID

  - The TSSPDCL (referred to as Employer in these documents) invites Bids for Construction of Compound Wall for newly allotted land of Uppal Bhagayat Phase-II layout, for proposed of new 33/11KV Sub-Station in Habsiguda Circle, Master Plan RR Circle of Master plan Zone (Reserved under Waddera/Sagara category). The Bidders should submit Bids for the works detailed in the table given in IFB.

  - The successful Bidder shall be expected to complete the works by the intended completion date specified in the Contract data.

- SOURCE OF FUNDS

2.1	The work is being taken up by TSSPDCL presently.

- ELIGIBLE BIDDERS

  - This Invitation for Bids is reserved under Waddera/Sagara category bidders.

  - Any materials, equipment, and services to be used in the performance of the Contract shall have their origin in India.

  - All Bidders shall provide in section 9, Forms of Bid and Qualification Information, a Statement that the Bidder is not associated, nor has been associated in the past, directly or indirectly, with the Consultant or any other entity that has prepared the design, specifications, and other documents for the Project or being proposed as project Manager for the Contract.  A firm that has been engaged by the Borrower to provide consulting services for the preparation or supervision of the works, and any of its affiliates shall not be eligible to Bid.

  - Government-owned enterprises in the Employer’s country may only participate if they are legally and financially autonomous, operate under commercial law and are not a dependent agency of the Employer.

  - Bidders who are under a declaration of ineligibility for corrupt and fraudulent practices issued by TSSPDCL in accordance with sub-clause 33 are not eligible.

- QUALIFICATION OF THE BIDDER

  - All Bidders shall provide in Section 9, Forms of Bid and Qualification Information, a preliminary description of proposed work method and schedule, including drawings and charts, as necessary.

  - All Bidders shall include the following information and documents with their Bids in Section 9 compulsorily. Otherwise the Bids will be evaluated based on the information available in the Bid.

- Copies of original documents defining the constitution or legal status, place of registration, and principal place of business, written power of attorney of the signatory of the Bid to commit the Bidder.

- Total monetary value of construction work performed for each of the last five years.

- Experience in works of a similar nature as specified in and size for each of the last five years, and details of works under way or contractually committed; and clients who may be contacted for further information on those contracts;

- Major items of construction equipment proposed to carry out the Contract;

- Reports on the financial standing of the Bidder, such as profit and loss statements and auditor’s reports for the past five years;

- Evidence of adequacy of working capital for this contract (access to letters of credit and availability of other financial resources);

- Authority to seek references from the Bidder’s bankers;

- Performance certificate for the works executed shall be furnished.

- The proposed methodology of construction, backed with their construction equipment planning and deployment, duly supported with broad calculations and quality control procedures proposed to be adopted, justifying their capability of achieving the completion of work as per milestones specified within the stipulated period of completion.

- Financial turnover should be supported by Income Tax return submitted to the Income Tax Department by the contractor.

4.3 (A) Mandatory:  To qualify for award of the contract, each Bidder in his name as a prime contractor should have the following in the last five years and the hard copies should be duly attested by gazette officer are to be submitted as part of technical Bid (Mandatory).

- Financial Turnover: (Mandatory)

As part of financial eligibility, the bidder has to submit the Last five financial year’s Financial turnover certificates tallying with the corresponding Turnover in the Profit & Loss Account, Balance sheets, Profit Loss statements certified by Chartered Accountant and income tax return statements i.e., from FY2017-18 to FY 2021-22 and the Bidder should have achieved an annual Financial Turn Over equal to 100 Percentage of the value of the Bid in any one Financial year during the last 5 FYs.

- Technical Experience: (Mandatory)

The bidder should upload a copy of the Experience Certificate of 100% value of work as Prime Contractor (in the same name) in any one financial year during the last five financial years. The work Experience certificate should be issued by an Engineer not below the cadre of Executive Engineer.

The bidder should upload a copy of the Experience Certificate of 50% of the prime quantities mentioned in any one financial year of the last five financial years which shall be as follows.

| Sl.No | Description | Quantity of the prime items | Quantity required (50% of the quantity) |
| --- | --- | --- | --- |
| 1. | RCC (Cu.m) (If slab quantity is in Sq.m, the same may be converted to Cu.m) | 37.41 Cu. m | 18.705 Cu. m |
| 2. | Steel (Metric Tons) | 3.367 MT | 1.6835 MT |
| 3. | Brick masonary | 54.03 Cu. m | 27.015 Cu. m |
| 4. | Plastering | 643.36 Sq m | 321.68 Sq m |

- Bid security 2% along  with the GST of ECV in the form of DD/Online payment/Bankers cheque in favour of Accounts officer, Master Plan, TSSPDCL, Hyderabad from any scheduled or nationalized bank. Alternatively, the Bidders may furnish a B.G (Nationalized Bank /Scheduled Bank acceptable to the Employer) in original in favour of Chief General Manager/ Master Plan/TSSPDCL, Hyd as per the pro forma attached and it should be valid for 6 months from the uploading starting date of the Bid. Fax/photocopies of the Bid security will not be accepted and will be rejected. The fact of having enclosed bid security by DD/BG along with the Bid should be clearly super scribed on the Bid envelope (Mandatory). Failure to furnish the Online receipt/Bank Guarantee along with Technical bid will entail rejection of bid.

- The bidder should upload a copy of the Contractor’s valid registration certificate in Civil works with any TS State or Central Government Departments and undertakings including registration of TSSPDCL, TSNPDCL, TSTRANSCO or TSGENCO. (Mandatory)

- The bidder must submit the Goods and services tax (GST) Registration certificate. (Mandatory)

- Self declaration (on letter head) by the Bidder in token of having gone through carefully and thoroughly all the terms and conditions mentioned in the Bid document and abide by all the terms and conditions clearly mentioning the name of the work or specification no. of the bid. (Mandatory)

- Liquid Assets/ Solvency Certificate for not less than 50% of Bid value and should have been issued by any scheduled bank or Nationalized bank not earlier than Twelve Months prior to the date of bid opening. The TSSPDCL reserves the right where ever necessary to make queries with the bidder’s bankers. (Mandatory)

- The bidder should upload a copy of EPF Registration Certificate. (Mandatory)

- The bidder should upload a copy of the ESI Registration Certificate. (Mandatory)

- The bidder should upload a Declaration (on letter head) to fulfill other statutory obligations as per the prevailing laws. Non compliance to the statutory obligations leads to termination of agreement (Mandatory).

- The bidder should upload the information of litigation history on letter head (Mandatory)

- Bidder must furnish the email address for correspondence (Mandatory).

- The bidder has to submit the educational Qualification and Experience certificates of Key person/Site in charge.

(i) Key person/Site in charge shall be a graduate Engineer in any discipline having minimum of five years experience in construction of Electrical Engineering works. (Mandatory)

(ii) Other than Key person/Site incharge
The Bidder should indicate skilled personnel list with minimum two years experience in construction of Electrical Engineering works. (Mandatory).

- Sub-contracting experience shall not be considered.

NOTE: The bidder shall Upload the attested hard copies (not below the rank/cadre of Executive Engineer) of all the above (a to k) mandatory documents and the same attested hard copies shall be submitted to the tender calling authority so as to reach on or before the date of opening of the Technical bid.

**The hard copies of above mandatory documents are to be placed in the order specified in the bid document.

4.3 B) OPTIONAL: 	The Bidder shall also furnish the following documents with its Bid or before issuing of the Letter of Intent.

- Firm Registration/Registered Partnership deed in case of firm. (Optional)

- PAN Card (Optional)

  - Even though the Bidders meet the above qualifying criteria, they are subject to be disqualified

and blacklisted if they have:

- made misleading or false representations in the forms, statements and attachments submitted in proof of the qualification requirements; and/or

b)  record of poor performance such as abandoning the works, not properly completing the contract, inordinate delays in completions or financial failures etc.

4.5     	All the materials to be utilized for the project should be subjected for inspection before dispatch. The Cost of the Inspection shall be borne by the Bidder. The contractor shall intimate the Employer, the bar chart for execution of works, enabling the CGM/ Master Plan/ TSSPDCL/Hyderabad to arrange for inspection of such works. The original invoices of purchases must be enclosed along with the bill for payment.

4.6	The Bidders have to furnish an undertaking in the prescribed format given in Section-9 disclosing their relationship with the officers/Chief General Managers of TRANSCO/ DISCOM failing which the tenders will be rejected. Any false information furnished in the declaration will render the contract liable for termination as well as recovery of damages.

4.7	Notwithstanding anything stated above the Employer reserves the right to assess capability and capacity of the Bidder to successfully execute the work covered under the package within stipulated completion period. This assessment shall inter-alia include (i) document verification (ii) Bidder’s work/ manufacturing facilities (iii) manufacturing capacity, details of work executed, works on hand, anticipated in future in addition to the works involved in present Bid (iv) details of plant and machinery, manufacturing and testing facilities, manpower and financial resources (v) details of quality systems in place (vi) past experience and performance (vii) customer feedback (viii) banker’s feedback etc.

5.  	COST OF BIDDING

5.1	The Bidder shall bear all costs associated with the preparation and submission of the Bid, and the Employer shall in no case be responsible and liable for those costs.

6.  	SITE VISIT

6.1	The Bidder, at the Bidder’s own responsibility and risk is required to visit & examine the Site of Works and its surroundings and obtain all information that may be necessary for preparing the Bid and entering into a contract for construction of the Works.  The costs of visiting the Site shall be at the Bidder’s own expense.

B. BIDDING DOCUMENTS

7.  	CONTENT OF BIDDING DOCUMENTS

7.1	The set of Bidding documents comprises the documents listed in the table below and addenda issued in accordance with Clause 9.

Section	    Invitation for Bids

- Instruction to Bidders

- Qualification Requirement

- Contract Data

- General Conditions of Contract

- Technical Specifications

- Quality assurance plan

- Schedule of quantities and prices

- Safety Measures

- Forms of Bid, Qualification Information and Forms of Securities

7.2	One set of schedule as original and other set (Xerox copy) as copy should be completed and submitted along with the Bid.

8.  	CLARIFICATION ON BIDDING DOCUMENTS

8.1	A prospective Bidder requiring any clarification of the Bidding documents may notify the Employer in writing or Email or Fax at the Employer’s address indicated in the invitation to Bid.  The Employer will respond to any request for clarification, which he received earlier than 7 days prior to the deadline for submission of Bids.  Copies of the Employer’s response will be forwarded to all prospective Bidders through e-procurement platform and also in TSSPDCL website, including a description of the enquiry but without identifying its source.

9.	AMENDMENT OF BIDDING DOCUMENTS

9.1	Before the deadline for submission of Bids, the Employer may modify the Bidding document by issuing addenda. The same will be communicated through e- procurement platform.

  - Any addendum thus issued shall be part & parcel of the Bidding document and shall be

communicated through e-procurement platform and also in TSSPDCL website.

  - To give prospective Bidders reasonable time in which addendum can be taken into account in preparing their Bids, the Employer shall extend as necessary deadline for submission of Bids, in accordance with Sub - Clause 19.2 and the same will be communicated through e-procurement platform.

C. PREPARATION OF BIDS

10.  	LANGUAGE OF THE BID

10.1	All documents relating to the Bid shall be in the English language

11.  	DOCUMENTS COMPRISING THE BID

  - The Bid submitted by the Bidder shall comprise the following in sealed covers superscribing Specification No., Bid security details, validity, Caste certificate (in case bid reserved for specific community) etc. and these shall be placed in another sealed cover.

- Bid Security as per clause 15 of ITB (Section-1)

- Technical Bid information (in the format indicated in Section 9 and any other materials required to be completed and submitted by Bidders in accordance with these instructions. The documents listed under Sections 3, 6 and 9 mentioned in Sub-Clause 7.1 of section-I shall be filled in without exception.

12.	BID PRICES

  - The contract shall be for the whole works as described in Sub-Clause 1.1.

    - The Bidder has to quote his rate which shall be inclusive of all costs of inspection and testing of equipment/material by the nominated representative of the employer for each batch of equipment/material manufacture on e-procurement site.

    - All duties, taxes  and other levies payable by the contractor under the contract, or for any other cause are excluded from the estimated prices, the Bidder shall verify the correctness and quote his price.

12.2 	N.A

12.3	Any variations in the statutory levies of taxes & duties shall be to the Bidder’s Account only.

12.4      The rates and prices quoted by the Bidder shall be firm.

12.4      The rates and prices quoted by the Bidder shall be firm.

13.  	CURRENCIES OF BID AND PAYMENT

13.1	In Indian Rupees only.

14.  	BID VALIDITY

  - Bids shall remain valid for a period not less than Ninety days (90) after the deadline date of Bid submission specified in Clause 19. “A Bid valid for a shorter period shall be rejected by the Employer as non-responsive.”

  - In exceptional circumstances, prior to expiry of the original time limit, the Employer may request that the Bidders to extend the period of validity for a specified additional period.  The request and the Bidder’s responses shall be made in writing or by e-mail or FAX. A Bidder may refuse the request without forfeiting his Bid security.  A Bidder agreeing to the request will not be required or permitted to modify his Bid, but will be required to extend the validity of his Bid security for a period of the extension, and in compliance with Clause 15 in all respects.

\

15.  	BID SECURITY

15.1	The Bidder shall furnish, as part of his Bid, a Bid security @ 2% along with 18% GST of Bid estimated value compulsorily. The amount is as shown in Sl.No.4 of the table of IFB for this particular work. This Bid security shall be in favour of Accounts Officer/ Master Plan /TSSPDCL/Gr.Hyderabad payable at Hyderabad in the form of DD from any scheduled Bank/Nationalized Bank or online payment on e-procurement platform. Alternatively the Bidders may furnish a B.G with  additional   GST @ 18% on Bank Guarantees  (Nationalized/Scheduled Bank acceptable to the Employer) in original in lieu of DD as per the proforma attached and it should be valid for 6 months from the uploading starting date of the Bid. Fax/photocopies of the Bid security will not be accepted and will be rejected. The fact of having enclosed bid security by DD/BG along with the Bid should be clearly super scribed on the Bid envelope.

15.2 	Any security other than the type of Bid security mentioned above will not be accepted.

15.3	Any Bid not accompanied by an acceptable Bid Security and not secured as indicated in Sub-Clauses 15.1 and 15.2 above shall be rejected by the Employer as non-responsive.

  - The Bid Security of the unsuccessful Bidder shall be returned within 28 days of the

end of the Bid validity period specified in Sub-Clause 14.1.

15.5	The Bid Security of the successful Bidder will be discharged when the Bidder has signed the Agreement and furnished the required performance Security.

15.6	The Bid Security may be forfeited

- if the Bidder withdraws the Bid after Bid opening during the period of Bid validity:

- if the Bidder does not accept the correction of the Bid Price, pursuant to Clause 26; or

- in the case of a successful Bidder, if the Bidder fails within the specified time limit to

- sign the Agreement or

- furnish the required performance Security.

16.   	ALTERNATIVE PROPOSALS BY BIDDERS

16.1	Bidders shall submit offers that comply with the requirements of the Bidding documents, including the basic technical design as indicated in the drawing and specifications.  Alternatives will not be considered.

17.	FORMAT AND SIGNING OF BID

17.1	The Bidder shall prepare one original and one copy of the documents comprising the Bid as described in Clause 11 of these Instructions to Bidders bound with the volume containing the Forms of Bid, and clearly marked “ORIGINAL” and “COPY” as appropriate.  In the event of discrepancy between them, the original shall prevail.

  - The original and copy of the Bid shall be typed or written in indelible ink and shall

be signed by a person or person duly authorized to sign on behalf of the Bidder, pursuant to Sub-Clauses 4.4.  All pages of the Bid where entries or amendments have been made shall be initialed by the person or persons signing the Bid.

  - The Bid shall contain no alterations or additions, except those to comply with instructions issued by the Employer, or as necessary to correct errors made by the Bidder, in which case such corrections shall be initialled by the person or persons signing the Bid.

  - The Bidder shall furnish information as described in the form of Bid on

Commissions or gratuities, if any, paid or to be paid to agents relating to this Bid and to contract execution if the Bidder is awarded the contract.

##### D. SUBMISSION OF BIDS

- SEALING AND MARKING OF BIDS

  - The Bidder shall seal the original and copy of the Bid in separate envelopes, duly marking the envelopes as “ORIGINAL” and “COPY”.  These envelopes (called as inner envelopes) shall then be put inside one outer envelope.

  - The inner and outer envelopes shall be addressed to the Employer at the following address:

The Chief General Manager/ Master Plan

TSSPDCL, Mint Compound,

Hyderabad -500063

and bear the following identification:

- Bid for System Improvement Project work in …………

- Bid security details

- Caste certificate if reserved category

- Bid Reference No.SKL (insert number)

- Do not open before (time and date for Bid opening, as per Clause 19)

  - In addition to the identification required in Sub-Clause 18.2, the inner envelopes shall indicate the name and address of the Bidder to enable the Bid to be returned unopened incase it is declared late, pursuant to Clause 20

18.4	If the outer envelope is not sealed and marked as above, the Employer shall assume no responsibility for the misplacement or premature opening of the Bid.

19.	DEADLINE FOR SUBMISSION OF THE BIDS

19.1	Bids (Hard Copy of uploaded documents only) must be received by the Employer at the address specified above not later than 12:00hrs on next working day of the Bid Submission closing date as given in the notice inviting Bid details above.

In the event of the specified date for the submission of Bids declared a holiday for the Employer, the Bids will be received up-to the appointed time on the next working day.

19.2	The Employer may extend the deadline for submission of Bids by issuing an amendment in accordance with Clause 9, in which case all rights and obligations of the Employer and the Bidders previously subject to the original deadline will then be subject to the new deadline.

- Late Bids: Hard copies received after the specified date & time, prescribed in Clause 19 even though the Bidder uploads the Bid in the e-procurement platform will be summarily rejected.

21.	MODIFICATION AND WITHDRAWAL OF BIDS

21.1	Bidders may modify or withdraw their Bids by giving notice in writing before the deadline prescribed in Clause 19.

21.2	Each Bidder’s modification or withdrawal notice shall be prepared, sealed, marked, and delivered in accordance with clause 17 & 18, with the outer and inner envelopes additionally marked “MODIFICATION” or “WITHDRAWAL” as appropriate.

21.3	No Bid may be modified after the deadline for submission of Bids.

21.4	Withdrawal or modification of a Bid between the deadline for submission of Bids and the expiration of the original period of Bid validity specified in Clause 14.1 above or as extended pursuant to Clause 14.2 may result in the forfeiture of the Bid security pursuant to Clause 15.

21.5	Bidders may only offer discounts to, or otherwise modify the prices of their Bids by submitting Bid modifications in accordance with this clause are included in the original Bid submission.

### E. BID OPENING AND EVALUATION

22.  	BID OPENING

22.1	The Employer will open all the Bids received (except those received late), including modification made pursuant to Clause 21, in the presence of the Bidders or their representatives who choose to attend at the time on the date and the place specified.  In the event of the specified date of Bid opening being declared a holiday for the Employer, the Bids will be opened at the appointed time and location on the next working day.

22.2	Bids for which an acceptable notice of withdrawal has been submitted pursuant to Clause 21 shall not be opened.

  - The Bidder’s names, the Bid prices, the total amount of each Bid and of any alternative Bid (if alternatives have been requested or permitted), any discounts, Bid modification and withdrawals, the presence or absence of Bid security, and such other details as the Employer may consider appropriate, will be announced by the Employer at the time of Bid opening, Any Bid price, discount, or alternative Bid price which is not read out and recorded at Bid opening will not be taken into account in Bid evaluation.

  - The Employer shall prepare minutes of the Bid opening, including the information disclosed to those present in accordance with Sub-Clause 22.3.

23.  	PROCESS TO BE CONFIDENTIAL

23.1	Information relating to the examination, clarification, evaluation, and comparison of Bids and recommendations for the award of a contract shall not be disclosed to Bidders or any other persons not officially concerned with such process until the award to the successful Bidder has been announced.  Any effort by a Bidder to influence the Employer’s processing of Bids or award decisions may result in the rejection of his Bid.

24.  	CLARIFICATION OF BIDS

24.1	To assist in the examination, evaluation, and comparison of Bids, the Employer may, at his discretion, ask any Bidder for clarification of his Bid, including breakup of unit rates.  The request for clarification and the response shall be in writing or by cable, but no change in the price or substance of the Bid shall be sought, offered, or permitted except as required to confirm the correction of arithmetic errors discovered by the Employer in the evaluation of the Bids in accordance with Clause 26.

24.2	Subject to sub-Clause 24.1, no Bidder shall contact the Employer on any matter relating to its Bid from the time of the Bidding opening to the time the contract is awarded.  If the Bidder wishes to bring additional information to the notice of the Employer, he should do so in writing.

  - Any effort by the Bidder to influence the Employer in the Bid evaluation, Bid comparison or contract award decisions may result in the rejection of the Bid.

25.  	EXAMINATION OF BIDS AND DETERMINATION OF RESPONSIVENESS

25.1	Prior to the detailed evaluation of Bids, the Employer will determine whether each Bid (a) meets the eligibility criteria defined in Clause 3; (b) has been properly signed; (c) is accompanied by the required securities and; (d) is substantially responsive to the requirements of the Bidding documents.

  - A substantially responsive Bid is one which conforms to all the terms, conditions and specifications of the Bidding documents, without material deviation or reservation.  A material deviation or reservation is one (a) which affects in any   substantial way the scope, quality, or performance of the Works; (b) which limits in any substantial way, inconsistent with the Bidding documents, the Employer’s rights or the Bidder’s obligations under the   Contract, or (c) whose rectification would affects unfairly the competitive position of other Bidders presenting substantially responsive Bids.

  - If a Bid is not substantially responsive, it will be rejected by the Employer, and may

not subsequently be made responsive by correction or withdrawal of the non-confirming deviation or reservation.

26.  	CORRECTION OF ERRORS

26.1	Bids determined to be substantially responsive will be checked by the Employer for any arithmetic errors.  Errors will be corrected by the Employer as follows:

- Where there is a discrepancy between the rates in figures and in words, the rate in words will govern, and

- Where there is a discrepancy between the unit rate and the line item total resulting from multiplying the unit rate by the quantity the unit rate as quoted will govern.

- Any discrepancy found to soft copy and hard copy, the soft copy will govern.

  - The amount stated in the Bid will be adjusted by the Employer in accordance with

the above procedure for the correction of errors and with the concurrence of the Bidder, shall be considered as binding upon the Bidder.  If the Bidder does not accept the corrected amount the Bid will be rejected, and the Bid security may be forfeited in accordance with Sub-Clause 15.6 (b).

27.  	EVALUATION AND COMPARISION OF BIDS

  - The Employer will evaluate and compare only the Bids determined to be substantially responsive in accordance with Clause 25.

  - In evaluating the Bids, the Employer will determine for each Bid the evaluated Bid

Price by adjusting the Bids price as follows:

- making any correction for errors pursuant to Clause 26; or

- making an appropriate adjustment for any other acceptable variations, deviations and making appropriate adjustments to reflect discounts or other price modifications offered in accordance with Sub Clause 21.5

  - The Employer reserves the right to accept or reject any variation, deviation, or alternative offer. Other factors which are in excess of the requirements of the Bidding documents or otherwise result in unsolicited benefits for the Employer shall not be taken into account in Bid evaluation.

  - If the Bid of the successful Bidder is seriously unbalanced in relation to the

Engineer’s estimate of the cost of work to be performed under the contract, the Employer may require the Bidder to produce detailed price analyses for any or all items of the Bill of Quantities, to demonstrate the internal consistency of those prices with the construction methods and schedule proposed.  After evaluation of the price analyses, the Employer may require that the amount of the performance security set forth in Clause 31.1 increased at the expense of the successful Bidder to a level sufficient to protect the Employer against financial loss in the event of default of the successful Bidder under the Contract.

### F. AWARD OF CONTRACT

- AWARD CRITERIA

  - Subject to Clause 31, the Employer will award the Contract to the Bidder whose Bid

has been determined to be substantially responsive to the Bidding documents and who has offered the lowest evaluated Bid Price, provided that such Bidder has been determined to be (a)eligible in accordance with the provisions of Clause 3, (b)qualified in accordance with the provisions of clause 4.

29.       EMPLOYER’S RIGHT TO ACCEPT ANY BID AND TO REJECT ANY OR

ALL BIDS

  - Notwithstanding Clause 28, the Employer reserves the right to accept or reject any

Bid, and to cancel the Bidding process and reject all Bids, at any time prior to the award of Contract, without thereby incurring any liability to the affected Bidder or Bidders or any obligation to inform the affected Bidder or Bidders of the grounds for the Employer’s action.

.

30.	NOTIFICATION OF AWARD AND SIGNING OF AGREEMENT

  - The Bidder whose Bid has been accepted will be notified of the award by the Employer prior to expiration of the Bid period by e-mail or by speed post. This letter (hereinafter in the Conditions of Contract called the “Letter of Intent”) will state the sum that the Employer will pay the Contractor in consideration of the execution, completion, and maintenance of the works by the contractor as prescribed by the Contract (hereinafter and in the Contract called the” Contract Price”).

  - The notification of award will constitute the formation of the Contract, subject only to the furnishing of a performance security in accordance with the provisions of Clause 31 and signing of agreement.

  - The contract agreement will incorporate all agreements between the Employer and the successful Bidder.  It will be signed by the Employer and sent to the successful Bidder, within 28 days following the notification of award along with the Letter of Acceptance.  The LOI will be sent to the successful bidder through email. The date of sending e mail will be taken as base date and the successful bidder will enter into agreement within 21 days from base date. If the bidder fails to do so the EMD will be forfeited.

  - Upon the furnishing by the successful Bidder of the performance Security, the Employer will promptly notify the other Bidders that their Bids have been unsuccessful.

  - The Bidder shall produce TIN (Tax Payer Identification Number) before issue of Letter of Acceptance.

- PERFORMANCE SECURITY

  - Within 21 days of receipt of the Letter of Acceptance, the Successful Bidder shall deliver to the Employer a Performance Security in any of the forms given below for an amount equivalent to 5% of the Contract price plus additional security for unbalanced Bids:

- shall be valid until a date 28 day from the date of expiry of Defects Liability period and the    additional security for unbalanced Bids shall be valid until a date 28days from the date of issue   of the certificate of completion.

-form given in section-9 or

-Bank draft, in favour of Accounts Officer / Master Plan / TSSPDCL / Gr.Hyderabad payable at Hyderabad drawn on any scheduled Bank/Nationalized Bank.

  - If the performance security is provided by the successful Bidder in the form of a Bank Guarantee, it shall be issued by a Nationalized Bank/Scheduled Bank and acceptable to the Employer.

  - Failure of the successful Bidder to comply with the requirements of Sub-Clause 31.1 shall constitute sufficient grounds for cancellation of the award and forfeiture of the Bid Security.

  - If the rates quoted is less than 90% of the estimated rates, then the successful Bidder has to give full performance guarantee for the amount which is less by 90% in addition to 5% standard performance security.

32.	MODE OF PAYMENT:

32.1	All payments shall be made on or after thirty (30) days of receipt of contractor’s invoice complete in all respects and supported by the requisite documents and fulfillment of stipulated conditions, if any. All the payment shall be released to the contractor through the Banks by crediting to his account.

32.2	All invoices under the contract shall be raised by the contractor on TSSPDCL and all payments shall be made to the contractor by Chief General Manager/ Master Plan on behalf of TSSPDCL.

33.  	CORRUPT OR FRAUDULENT PRACTICES.

- TSSPDCL Bidders/ Contractors/ Contractors observe the highest standard of ethics during the procurement and execution of such contracts.  In pursuance of this policy, TSSPDCL:

- Defines, for the purposes of this provision, the terms set forth as follows:

    - “Corrupt Practice” means the offering, giving, receiving or soliciting of any thing of value to influence the action of a public official in the work awarding process or in contract execution, and

    - “Fraudulent Practice” means a misrepresentation of facts in order to influence work awarding process or the execution of a contract to the detriment of the Employer and includes collusive practice among Bidders (prior to or after Bid submission) designed to establish Bid prices at artificial non-competitive levels and to deprive the Employer of the benefits of free and open competition.

- Will reject a proposal for award if it determines that the Bidder recommended for award is involved in corrupt or fraudulent practices in competing for the contract in question.

- Will declare a firm ineligible, either indefinitely or for a stated period of time, if it at any time the firm is engaged in corrupt or fraudulent practices in competing for, or in executing a Bank-financed contract.

34.	QUALITY ASSURANCE PLAN:

34.1	The quality assurance plan of contractor shall be generally in accordance with ISO-9000/IS-14000. This information shall be furnished with his Bids as per section-6, failing which his Bid shall be liable for rejection.

SECTION -2

QUALIFICATION REQUIREMENT

QUALIFICATION REQUIREMENT

To qualify for award of the contract, each Bidder in his name as a prime contractor should have in the last five years the qualification requirement given in Clause No.  4.3 of Instructions to bidders as above.

SECTION 3

CONTRACT DATA

CONTRACT DATA

Items marked “N/A” do not apply in this Contract.

The following documents are also part of the Contract:		    	Clause ref of G.C.C.

Reference

- The Schedule of Operating and Maintenance Manuals			           	(51)

- The Schedule of other Contractors						(7)

- The Schedule of Key Personnel.							(8)

The above insertions should correspond to the information provided in the Invitation of Bids.

The Employer is

Name		:     	Chief General Manager /Master Plan

Address	:    	Southern Power Distribution Company of Telangana Limited,

Mint Compound,

Hyderabad - 500063.

Name of Authorized Representative: Superintending Engineer/Master Plan/ Ranga reddy.

The Engineer is										(1.1)

Name		:	Executive Engineer /MP/ RR

Address	: 	Mint Compound, Hyderabad

The name and identification number of the Contract is Bid No.

BID No. Chief General Manager/Master Plan/GH/TSSPDCL: 06-A/2022-23

(Insert name and number as indicated in the Invitation for Bids (or Pre-qualification, if any).

The works consist of  Construction of Compound Wall for newly allotted land of Uppal Bhagayat Phase-II layout, for proposed of new 33/11KV Sub-Station in Habsiguda Circle, Master Plan RR Circle of Master plan Zone (Reserved under Waddera/Sagara category)

(Brief Summary, including relationship to other contracts under the project)

The Start Date shall be Date of Issue of Letter of Intent.     				(1.1)

The Intended Completion Date for the whole

of the Works is Four months from the start date.					(16, 25, 26)

The following documents also part of the Contract					(2.3)

The Contractor shall submit a revised Program for the Works

within 15 days of delivery of the Letter of proceeding to work.			 	(25)

The Site Possession Dates shall be:					              	(20)

Within a month after entering into Agreement

The Site is located at	___________________			               		  (1)

And is defined in drawings on.___________________________

The Defects Liability Period is one year from the date of issue of completion certificate.  (32)

The minimum insurance cover for physical property, injury	 	 (12)

and death is Five (lakhs) per occurrence with the number of occurrences

limited to four. After each occurrence, contractor will pay additional premium

necessary to make insurance valid for four occurrences always. or as per TSSPDCL orders

The Compensation Events.	  		(41)

The period between program updates shall be 30 days.				  		(25)

The amount to be withheld for late submission of an updated			 		 (25)

program shall be Rs. 25,000/-

The language of the Contract documents is English				  		 (3)

The law which applies to the Contract is the law of India				   		 (3)

The currency of the Contract is Indian Rupees. 					 		 (43)

Institution whose arbitration procedures shall be used: 				 		 (24)

Arbitration will take place in accordance with Indian Arbitration Conciliation act 1996. (24)

The proportion of payments retained (retention money) shall be 10% from each bill

subject to a maximum of 5% of contract value. Item wise payments will be made 	(44)

95% payment will be made on or after successful completion and commissioning of the contract work and progress bills will be admitted accordingly.

The liquidated damages for whole of the works are at the rate of Rs. ½ % per week on left over, subject to the maximum amount of liquidated damages, for the whole of the works is 5% of final contract price.							    		 (45)

SECTION – 4

GENERAL CONDITIONS OF CONTRACT

GENERAL CONDITIONS OF CONTRACT

TABLE OF CONTENTS

| A. GENERAL | Page No. | C. QUALITY CONTROL | Page No. |
| --- | --- | --- | --- |
| 1. Definitions | 34 | 30. Identifying Defects | 40 |
| 2. Interpretation | 35 | 31. Tests | 40 |
| 3. Language and Law | 36 | 32. Correction of Defects | 40 |
| 4. Engineer’s Decisions | 36 | 33. Uncorrected Defects | 40 |
| 5. Delegation | 36 |  |  |
| 6. Communications | 36 | D. COST CONTROL |  |
| 7. Other Contractors | 36 | 34. Quantities and Prices | 41 |
| 8. Personnel | 36 | 35. Changes in the Quantities | 41 |
| 9. Employer’s & Contractor’s Risks | 36 | 36. Variations | 41 |
| 10. Employer’s Risks | 36 | 37. Payments for Variations | 41 |
| 11. Contractor’s Risks | 37 | 38. Cash Flow Forecasts | 42 |
| 12. Insurance | 37 | 39. Payment Certificates | 42 |
| 13. Site Investigation Reports | 37 | 40. Payments | 42 |
| 14. Queries about the Contract Data | 37 | 41. Compensation Events 42. Tax | 42 43 |
| 15. Contractor to Construct the Works | 37 | 43. Currencies | 43 |
| 16. The Works to be completed by the Intended Completion Date | 37 | 44. Retention 45. Liquidated Damages | 43 43 |
| 17. Approval by the Engineer | 38 | 46. Securities | 44 |
| 18. Safety | 38 | 47. Cost of Repairs | 44 |
| 19. Discoveries | 38 |  |  |
| 20. Possession of the Site | 38 | E. FINISHING THE CONTRACT |  |
| 21. Access to the Site | 38 |  |  |
| 22. Instructions | 38 | 48. Completion | 44 |
| 23. Disputes | 38 | 49. Taking Over | 44 |
| 24. Procedure for Disputes | 38 | 50. Final Account | 44 |
|  |  | 51. Operating and Maintenance Manuals | 45 |
| B. TIME CONTROL |  | 52. Termination 53. Payment upon Termination | 45 46 |
| 25. program | 39 | 54. Property | 46 |
| 26. Extension of the Intended Completion Date | 39 | 55. Release of Performance | 46 |
| 27. Delays Ordered by the Meetings | 39 | 56.Suspension of loan or credit by Financier | 46 |
| 28. Management Meetings | 39 | F. SPECIAL CONDITIONS OF CONTRACT | 47 |
| 29. Early Warning | 40 |  |  |

F.     SPECIAL CONDITIONS OF CONTRACT

TABLE OF CONTENTS

| S. NO. | ITEM |
| --- | --- |
| 1. | DESCRIPTION |
| 1.1A | RESPONSIBILITY FOR EXECUTION OF THE CONTRACT |
| 1.1B | NOTICES |
| 2. | WORKING HOURS |
| 3. | EXTRA SHIFTS AND OVER TIME WORK |
| 4. | ACCIDENTS |
| 5. | INDEMNITIES |
| 6. | LICENSE |
| 7. | TRANSPORT ARRANGEMENT |
| 8. | MACHINERY TOOLS AND TACKLES |
| 9. | SAFETY PRECAUTIONS |
| 10. | FIRE PRECAUTIONS |
| 11. | WORKING AREA AND CLEANLINESS |
| 12. | SITE DISCIPLINE |
| 13. | SITE OFFICE AND SITE STORES |
| 14. | APPROVAL OF INSTALLATION BY GOVERNMENT AUTHORITIES (CEIG) |
| 15. | MEASUREMENT OR WORK |
| 16. | INCOME TAX |
| 17. | TERMINATION OF CONTRACT FOR BOARDS CONVENIENCE |
| 18. | LABOUR |
| 19. | COMPLIANCE WITH LABOUR REGULATIONS |
| 20. | ARBITRATION |
| 21. | RESPONSIBILITY FOR EXECUTION OF THE CONTRACT |

CONDITIONS OF CONTRACT

##### GENERAL

- DEFINITIONS

  - Terms which are defined in the Contract Data are also defined in the Conditions of contract but keep their defined meanings.  Capital initials are used to identify defined terms.

Compensation Events are those defined in Clause 41 hereunder.

The Completion Date is the date of completion of the Works as certified by the Engineer in accordance with Clause 48

The Contract is the contract between the Employer and the Contractor to execute, complete and maintain the Works.  It consists of the documents listed in Clause 2.3 below.

The Contract Data defines the documents and other information, which comprise the Contract.

The Contractor is a person or corporate body whose Bid to carry out the Works has been accepted by the Employer.

The Contractor’s Bid is the completed Bidding documents submitted by the Contractor to the Employer.

The Contract Price is the price stated in the Letter of Acceptance and thereafter as adjusted in accordance with the provisions of the Contract.

Days are calendar days; months are calendar months.

A defect is any part of the Works not completed in accordance with the Contract.

The Defects Liability period is the period named in the Contract Data and calculated from the Completion Date.

The Employer is the party who will employ the Contractor to carry out the Works.

The Engineer is the person named in the Contract Data (or any other competent person appointed and notified to the contractor to act in replacement of the Engineer) who is responsible for supervising the Contractor, administering the Contract, certifying payments due to the Contractor, issuing and valuing variations to the contract, awarding extensions of time, and valuing the Compensation Events.

Equipment is the Contractor’s machinery and vehicles brought temporarily to the Site to construct the Works.

The initial Contract Price is the Contract Price listed in the Employer’s Letter of Acceptance.

Charging Date: It is the date on which all the works awarded are completed in full shape and handed over to the Employer or the Engineer.

The Intended Completion Date is the date on which it is intended that the Contractor shall complete the Works.  The Intended Completion Date is specified in the Contract Data.  The Intended Completion Date may be revised only by the Engineer by issuing an extension of time.

Materials are all supplies, including consumables, used by the contractor for incorporation in the Works.

Plant is any integral part of the Works, which is to have a mechanical, electrical, electronic or chemical or biological function.

The Site is the area defined as such in the Contract Data.

Site Investigations Reports are those which were included in the Bidding documents and are factual interpretative reports about the surface and sub-surface conditions at the site.

Specifications mean the Specification of the Works included in the Contract and any modification or addition made or approved by the Engineer.

The Start Date is given in the Contract Data.  It is the date when the Contractor shall commence execution of the works.  It does not necessarily coincide with any of the Site Possession Dates.

Temporary Works are works designed, constructed, installed, and removed by the Contractor, which are needed for construction or installation of the Works.

A Variation is an instruction given by the Engineer, which varies the Works.

The Works are what the Contract requires the contractor to construct, install, and turn over to the Employer, as defined in the Contract Data.

- INTERPRETATION

  - In interpreting these Conditions of Contract, singular also means plural, male also means female or neuter, and the other way around.  Headings have no significance.  Words have their normal meaning under the language of the Contract unless specifically defined.  The Engineer will provide instructions clarifying queries about the Conditions of Contract.

  - If sectional completion is specified in the Contract Data, references in the Conditions of Contract to the Works, the Completion Date, and the Intended Completion Date apply to any Section of the works (other than references to the Completion Date and Intended Completion date for the whole of the Works).

  - The documents forming the Contract shall be interpreted in the following order of priority:

- Agreement

- Letter of Acceptance, notice to proceed with the works

- Contractor’s Bid

- Contract Data

- Conditions of Contract

- Specifications

- Drawings

- Price Bid document where quantities and their estimated values are mentioned.

- Any other document listed in the Contract Data as forming part of the Contract.

- Amendments/ Pre-Bid decision, if any.

3.  	LANGUAGE AND LAW

  - The language of the Contract and the law governing the Contract are stated in the Contract Data.

4.   	ENGINEERS DECISIONS

4.1	Except where otherwise specifically stated, the Engineer will decide contractual matters between the Employer and the Contractor in the role representing the Employer.

- DELEGATION

  - The Engineer may delegate any of his duties and responsibilities to other people except to the Adjudicator after notifying the Contractor and may cancel any delegation after notifying the contractor.

- COMMUNICATIONS

  - Communications between parties which are referred to in the conditions are effective only when in writing.  A notice shall be effective only when it is delivered (in terms of Indian Contract Act).

7	 OTHER CONTRACTORS

7.1	The Contractor shall cooperate and share the Site with other contractors, public authorities, utilities, and the Employer between the dates given in the Schedule of Other Contractors.  The Contractor shall as referred in the Contract data, also provide facilities and services for them as described in the Schedule.  The employer may modify the schedule of other contractor and shall notify the contractor of any such modification.

8.         	PERSONNEL

  - The Contractor shall employ the key personnel named in the Schedule of Key Personnel as referred to in the Contract Data to carry out the functions stated in the Schedule to other personnel approved by the Engineer.  The Engineer will approve any purposed replacement of Key personnel only if their qualifications, abilities, and relevant experience are substantially equal to or better than those of the personnel listed in the Schedule.

  - If the Engineer asks the Contractor to remove a person who is a member of the Contractor’s staff or his work force stating the reasons the Contractor shall ensure that the person leaves the site within seven days and has no further connection with the work in the Contract.

9. 	EMPLOYER’S AND CONTRACTORS RISKS

9.1	The Employer carries the risks which this Contract states are Employer’s risks, and the Contractor carries the risks which this Contract states are Contractor’s risks.

- EMPLOYER’S RISKS

  - The Employer is responsible for the exceptional risks which are (a) in so far as they directly affect the execution of the Works in the Employer’s country, the risks of war, hostilities, invasion, act of foreign enemies, rebellion, revolution, insurrection or military or usurped power, civil war, riot commotion or disorder (unless restricted to the Contractor’s employees), and contamination from any nuclear fuel or nuclear waste or radioactive toxic explosive, or (b) a cause due solely to the design of the Works, other than the Contractor’s design.

- CONTRACTOR’S RISKS

  - All risks of loss of or damage to physical property and of personal injury and death, which arise during and in consequence of the performance of the Contract and other than excepted risks, are the responsibility of the Contractor.

- INSURANCE

  - The Contractor shall provide, in the joint names of the Employer and the Contractor, insurance cover from the start Date to the end of the Defects Liability Period, in the amounts and deductibles stated in the Contract Data for the following events which are due to the Contractor’s risks:

- Loss of or damage to the Works, Plant and Materials;

- Loss of or damage to Equipment

- Loss of or damage of property (except the Work, Plant, Materials and Equipment) in connection with the Contract; and

- Personal injury or death.

  - Policies and certificates for insurances shall be delivered by the Contractor to the Engineer for the Engineer’s approval before the Start Date.  All such insurance shall provide for compensation to be payable in the types and proportions of currencies required to rectify the loss or damage incurred.

  - If the Contractor does not provide any of the policies and certificates required, the Employer may effect the insurance which the Contractor should have provided and recover the premiums the Employer has paid from payments otherwise due to the Contractor or, if no payment is due, the payment of the premiums shall be a debt due.

  - Alterations to the terms of insurance shall not be made without the approval of the Engineer.

  - Both parties shall comply with any conditions of the insurance policies.

- SITE INVESTIGATION REPORTS

  - The Contractor, in preparing the Bid, shall rely on any site Investigation Reports referred to in the Contract Data, supplemented by any information available to the Bidder.

- QUERIES ABOUT THE CONTRACT DATA

  - The Engineer will clarify queries on the Contract Data.

- CONTRACTOR TO CONSTRUCT THE WORKS

  - The Contractor shall construct and install the Works in accordance with the Specifications and Drawings.

- THE WORKS TO BE COMPLETED BY THE INTENDED COMPLETION DATE

  - The Contractor may commence execution of the Works on the Start Date and shall carry out the Works in accordance with the program submitted by the Contractor as updated with the approval of the Engineer and complete them by the intended completion Date.

- APPROVAL BY THE ENGINEER

  - The Contractor shall submit Specifications and Drawings showing the proposed Temporary Works to the Engineer, who is to approve them if they comply with the Specifications and Drawings.

  - The Contractor shall be responsible for design of Temporary Works.

  - The Engineer’s approval shall not alter the Contractor’s responsibility for design of the Temporary Works.

  - All Drawings prepared by the Contractor for the execution of the temporary or permanent Works are subject to prior approval by the Engineer before their use.

- SAFETY

  - The Contractor shall be responsible for the safety of all activities on the Site.

- DISCOVERIES

  - Anything of historical or other interest or of significant value unexpectedly discovered on the Site is the property of the Employer.  The Contractor is to notify the Engineer of such discoveries and carry out the Engineer’s instructions for dealing with them.

- POSSESSION OF THE SITE

  - The Employer shall give possession of all parts of the Site to the Contractor by the date stated in the Contract Data, for execution of works.

- ACCESS TO THE SITE

  - The Contractor shall allow the Engineer and any person authorized by the Engineer access to the Site, to any place where work in connection with the Contract is being carried out or is intended to be carried out and to any place where materials or plant are being manufactured/fabricated/assembled for the works.

- INSTRUCTIONS

  - The Contractor shall carry out all instructions of the Engineer which comply with the applicable laws where the Site is located.

  - The Contractor shall permit the bank to inspect the Contractor’s accounts and records relating to the performance of the Contractor and to have them audited by auditors appointed by the Bank, if so required by the Bank.

- DISPUTES

  - If the Contractor believes that a decision taken by the Engineer was whether outside the authority given to the Engineer by the Contract or that the decision was wrongly taken, the decision shall be referred to the Arbitrator within 14 days of the notification of the Engineer’s decision.

- PROCEDURE FOR DISPUTES

  - The arbitration shall be conducted in accordance with the arbitration procedure published by the institution named and, in the place, shown in the Contract Data.

B. TIME CONTROL

- PROGRAM

  - The Bidder should prepare the month wise programme schedule to complete the proposed work with in specified period of 4 months and submit along with the Bid. The Bidder must invariably stick on to the programme submitted, if contract is awarded. No deviations will be entertained in this regard. The schedule programme submitted by the Bidder will also be considered as part and part of the agreement.

  - Within the time stated in the Contract Data the Contractor shall submit to the Engineer for approval a program showing the general methods, arrangements, order, and timing for all the activities in the Works along with monthly cash flow forecast.

  - An update of the Program shall be a program showing the actual progress achieved on each activity and the effect of the progress achieved on the timing of the remaining work including any changes to the sequence of the activities.

  - The Contractor shall submit to the Engineer, for approval, an updated program at intervals no longer than the period stated in the Contract Data.  If the Contractor does not submit an updated program within this period, the Engineer may withhold the amount stated in the Contract Data from the next payment certificate and continue to withhold this amount until the next payment after the date on which the overdue program has been submitted.

  - The Engineer’s approval of the Program shall not alter the Contractor’s obligations.  The Contractor may revise the Program and submit it to the Engineer again at any time.  A revised Program is to show the effect of variations and Compensations Events.

- EXTENSION OF THE INTENDED COMPLETION DATE

  - The Engineer shall extend the Intended Completion Date if a Compensation Event occurs or a variation is issued which makes it impossible for Completion to be achieved by the intended Completion Date without the Contractor taking steps to accelerate the remaining work and which would cause the Contractor to incur additional cost.

  - The Engineer shall decide whether and by how much to extend the Intended Completion Date within 21 days of the Contractor asking the Engineer for a decision upon the effect of a Compensation Event or variation and submitting full supporting information.  If the Contractor has failed to give early warning of a delay or has failed to cooperate in dealing with delay, the delay by this failure shall not be considered in assessing the new intended Completion Date.

- DELAYS ORDERED BY THE MEETINGS

  - The Engineer may instruct the Contractor to delay the start or progress of any activity within the Works.

- MANAGEMENT MEETINGS

  - Either the Engineer or the Contractor may require the other to attend management meeting.  The business of a management meeting shall be to review the plans for remaining work and to deal with matters raised in accordance with the early warning procedure.

  - The Engineer shall record the business of management meetings and is to provide copies of his record to those attending the meeting and to the Employer.  The responsibility of the parties for

actions to be taken is to be decided by the Engineer either at the management meeting or after the management meeting and stated in writing to all who attend the meeting.

- EARLY WARNING

  - The Contractor is to warn the Engineer at the earliest opportunity of specific likely future events of circumstances that may adversely affect the quality of the work, increase the Contract Price or delay the execution of works.  The Engineer may require the Contractor to provide an estimate of the expected effect of the future event or circumstance on the Contract Price and Completion Date.  The estimate is to be provided by the Contractor as soon as reasonably possible.

  - The Contractor shall cooperate with the Engineer in making and considering proposals for how the effect of such an event or circumstance can be avoided or reduced by anyone involved in the work and in carrying out any resulting instruction of the Engineer.

C.QUALITY CONTROL

- IDENTIFYING DEFECTS

  - The Engineer shall check the Contractor’s work and notify the Contractor of any Defects that are found. Such checking shall not affect the Contractor’s responsibilities.  The Engineer may instruct the Contractor to search for a Defect and to uncover and test any work that the Engineer considers may have a Defect.

  - The Engineer concerned of the department shall counter check the quality of work before taking over the works prior to charging apart from this, a 3rd party inspection shall be done (other than department).

- TESTS

If the Engineer instructs the contractor to carry out a test not specified in the Specification to check whether any work has a Defect and the test shows that it does, the Contractor shall pay for the test and any samples.  If there is no Defect the test shall be a Compensation Event.

- CORRECTION OF DEFECTS

  - The Engineer shall give notice to the Contractor of any Defects before the end of the Defects Liability Period, which begins at Completion and is defined in the Contract Data.  The Defects Liability period shall be extended for as long as Defects remain to be corrected.

32.2     	Every time notice of a Defect is given; the Contractor shall correct the notified defect within the length of time specified by the Engineer’s notice.

33 	UNCORRECTED DEFECTS

33.1	If the Contractor has not corrected a Defect within the time specified in the Engineer’s, the Engineer will assess the cost of having the Defect corrected, and the Contractor will pay this amount and it will be recovered from his future bills.

D.COST CONTROL

- QUANTITIES AND PRICES

  - The schedule-A (price Bid) shall contain quantities covered under all items for the supply, construction, installation, testing, and commissioning work to be done by the Contractor.

  - The schedule-A (price Bid) is used to calculate the Contract Price.  The Contractor is paid for the quantity of the work done at the rate in the schedule-A (price Bid) for each item accordingly, for the actual executed quantity only.

35       	CHANGES IN THE QUANTITIES

35.1     	If the final quantity of the work done differs from the quantity in the Schedule-A for the particular item by more than 25 percent provided the change not exceeds 1% of   Initial Contract Price, the Engineer shall adjust the rate to allow for the change.

  - The Engineer shall not adjust rates from changes in quantities if thereby the initial Contract   Price is exceeded by more than 10 percent, except with the Prior approval of the Employer.

  - If requested by the Engineer, the Contractor shall provide the Engineer with a detailed cost break up of any rate in the schedule-A, or cost data.

36	VARIATIONS

36.1    	All variations shall be included in updated program produced by the Contractor.

37	 PAYMENTS FOR VARIATIONS

37.1    	The Contractor shall provide the Engineer with a quotation for carrying out the Variation when requested to do so by the Engineer.  The Engineer shall assess the quotation, which shall be given within seven days of the request or within any longer period stated by the Engineer and before the Variation is ordered.

  - If the work in the Variation corresponds with an item description in the schedules and if, in the opinion of the Engineer, the quantity of work above the limit stated in Sub Clause 35.1 or the timings of its execution do not cause the cost per unit of quantity the rate in the schedule-A shall be used to calculate the value of the Variation.  If the cost per unit of quantity changes, or if the nature or timing of the work in the Variation does not correspond with items in the schedules, the quotation by the Contractor shall be in the form of new rates for the relevant items of work.

  - Out of the Rate/Unit & lump sum rates the contractor shall be paid for the lowest price i.e.   which ever is less.

  - If the Contractor’s quotation is unreasonable, the Engineer may order the variation and make      a change to the Contract Price, which shall be based on Engineer’s own forecast of the effects of the Variation on the Contractor’s costs.

  - If the Engineer decides that the urgency of varying the work would prevent a quotation being given and considered without delaying the work, no quotation shall be given and the Variation shall be treated as Compensation Event.

- CASH FLOW FORECASTS

  - When the Program is updated, the Contractor is to provide the Engineer with an updated cash flow forecast.

- PAYMENT CERTIFICATES

  - The Contractor shall submit to the Engineer monthly statements of the estimated value of work completed less the cumulative amount certified previously.

  - The Engineer shall check the Contractor’s monthly statement within 14 days and certify the amount to be paid to the Contractor after taking into account any credit or debit for the month in question in respect of materials for the works in the relevant amounts.

  - The value of work executed shall be determined by the Engineer.

  - The value of work executed shall comprise the value of the quantities of the items in the schedule-A completed.

  - The value of work executed shall include the valuation of Variations and Compensation Events.

  - The Engineer may exclude any item certified in a previous certificate or reduce the proportion of any item previously certified in any certificate in the light of later information.

- PAYMENTS

  - Payments shall be adjusted for deductions, retention and other recoveries in terms of

the contract and deduction at source of taxes as applicable under the law. The Employer shall

pay the Contractor the amounts certified by the Engineer on or after 30 days of the date of each certificate.

  - Items of the Works for which no rate or price has been entered, it will not be paid for by the Employer and shall be treated as deemed to be covered by other rates and prices in the Contract.

- COMPENSATION EVENTS

  - The following are Compensation Events unless they are caused by the Contractor:

- The Employer does not give access to a part of the Site by the Site Possession Date stated in the Contract Data.

- The Employer modifies the schedule of other contractors in a way, which affects the work of the contractor under the contract.

- The Engineer orders a delay or does not issue drawings, specifications or instructions required for execution of works on time.

- The Engineer instructs the Contractor to uncover or to carry out additional tests upon work, which is then found to have no Defects.

- Ground conditions are substantially more adverse than could reasonably have been assumed before issuance of Letter of Acceptance from the information issued to Bidders (including the Site Investigation Reports), from information available publicly and from a visual inspection of the Site.

- The Employer gives an instruction for dealing with an unforeseen condition, caused by the Employer, or addition works required for safety or other reasons.

- Other contractors, public authorities, utilities or the Employer does not work within the dates and other constraints stated in the Contract, and they cause delay or extra cost to the Contractor.

- The effect on the Contractor of any of the Employer’s Risks.

- The Engineer unreasonably delays issuing a Certificate of Completion.

(j)	Other Compensation Events listed in the Contract Data or mentioned in the Contract if any.

  - If a Compensation Event would cause additional cost or would prevent the work being completed before the intended Completion Date, the Contract Price shall be increased and/or the Intended Completion Date is extended.  The Engineer shall decide whether and by how much the Contract Price shall be increased and whether by how much the Intended Completion Date shall be extended.

  - As soon as information demonstrating the effect of each Compensation Event upon the Contractor’s forecast cost has been provided by the Contractor, it is to be assessed by the Engineer and the Contract Price shall be adjusted accordingly.  If the Contractor’s forecast is deemed unreasonable, the Engineer shall adjust the Contract Price based on Engineer’s own forecast.  The Engineer will assume that the Contractor will react competently and promptly to the event.

  - The Contractor shall not be entitled to compensation to the extent the Employer’s interest are adversely affected by the Contractor not having given early warning or not having cooperated with the Engineer.

- TAX

  - Goods and services tax (GST) as applicable (prevailing now and applicable as and when amended)

- CURRENCIES

  - All payments shall be made in Indian Rupees.

44.		RETENTION

44.1	The Employer shall retain 10% from each payment due to the Contractor as stated in the Contract Data, subject to a maximum of 5% of contract value.

44.2	On Completion of the whole of the Works and on submitting all Operation and Maintenance Manuals, 50% of the total amount retained is returned to the Contractor and balance 50% after Defects Notice Period and the Employer has certified that all Defects notified by him to the Contractor before the end Defect Liability period have been corrected.

45.	LIQUIDATED DAMAGES

45.1	The Employer shall retain from each payment due to the Contractor the proportion stated in the contract Data until Completion of the whole of the Works.

45.2    On completion of the whole of the Works 50% of the total amount retained is paid to the Contractor.

45.3	The Contractor shall pay liquidated damages to the Employer at the rate per week stated in the Contract Data for each week that the Completion Date is later than the intended Completion Date (for the whole of the works or milestone as stated in the contract Data).  The total amount of liquidated damages shall not exceed the amount defined in the Contract Data.  The Employer may deduct liquidated damages from payments due to the Contractor.  Payment of liquidated damages does not affect the Contractor’s liabilities.

45.4	If the Intended Completion Date is extended after liquidated damages have been paid, the Engineer shall correct any overpayment of liquidated damages by the Contractor by adjusting the next payment certificate.

46.       SECURITIES

  - The Performance Security (including additional security for unbalanced Bids) shall be

provided to the Employer not later than the date specified in the Letter of Acceptance and shall be issued in an amount and form and by a bank or surety acceptable to the Employer and denominated in Indian Rupees.  The Performance Security shall be valid until a date 28 days from the date of expiry of Defects Liability period and the additional security for unbalanced Bids shall be valid until a date 28days from the date of issue of the certificate of completion.

47.      	COST OF REPAIRS

  - Loss of damage to the Works or Materials to be incorporated in the Works between the Start Date and the end of Defects correction periods shall be remedied by the Contractor at the Contractor’s cost if the loss or damage arises from the Contractor’s acts or omissions.

E. FINISHING THE CONTRACT

- COMPLETION

48.1	The Contractor shall request the Engineer to issue a Certificate of Completion of the Works and the Engineer will do so upon deciding that the work is completed in all respects.

49. 	TAKING OVER

  - The Employer shall take over the Site and the Works within seven days of the Engineer issuing a certificate of completion.

50.	FINAL ACCOUNT

  - The Contractor shall supply to the Engineer a detailed account of the total amount that the Contractor considers payable under the contract before the end of the Defects Liability Period.  The Engineer shall issue a Defect Liability Certificate and certify any final payment that is due to the Contractor within 56 working days of receiving the Contractor’s account if it is correct and complete.  If it is not, the Engineer shall issue within 56 working days a schedule that states that scope of the corrections or additions that are necessary.  If the Final Account is still unsatisfactory after it has been resubmitted, the Engineer shall decide on the amount payable to the Contractor and issue a payment certificate, within 56 working days of receiving the Contractor’s revised account.

51.	OPERATING AND MAINTENANCE MANUALS

  - If “as built” Drawings and/or operating and maintenance manuals are required, the

Contractor shall supply them by the dates stated in the Contract Data.

51.2      If the Contractor does not supply the Drawings and/or manuals by the dates stated in the Contract Data, or they do not receive the Engineer’s approval, the Engineer shall withhold the amount stated in the Contract Data from payment due to the Contractor.

- TERMINATION

  - The Employer or the Contractor may terminate the Contract if the either party causes a fundamental breach of the Contract.

  - Fundamental breaches of Contract include but shall not be limited to the following.

- The Contractor stops work for 28 days when no stoppage of work is shown on the current programme and the stoppage has not been authorized by the Engineer.

- The Engineer instructs the Contractor to delay the progress of the Works and the instruction is not withdrawn within 28 days.

- The Employer or the Contractor is made bankrupt or goes into liquidation other than for reconstruction or amalgamation.

- A payment certified by the Engineer is not paid by the Employer to the Contractor within 120 days of the date of the Engineer’s certificate:

- The Engineer gives Notice that failure to correct a particular Defect is a fundamental breach of Contract and the Contractor fails to correct it within a reasonable period of time determined by the Engineer.

- The Contractor does not maintain a security which is required;

- The Contractor has delayed the completion of works by the number of days for which the maximum amount of liquidated damages can be paid as defined in the Contract data; and

- If the Contractor, in the judgment of the Employer has engaged in corrupt or fraudulent practices in competing for or in the executing the Contract.

For the purpose of this paragraph: “corrupt practice” means the offering, giving receiving or soliciting of any thing of value to influence the action of a public official in the procurement process or in contract execution.  “Fraudulent Practice” means a misrepresentation of facts in order to influence a procurement process or the execution of a contract to the detriment of the Borrower and includes collusive practice among Bidders (prior to or after Bid submission) designed to establish Bid prices at artificial non-competitive levels and to deprive the Borrower of the benefits of free and open competition.

  - When either party to the Contract gives notices of a breach of contract to the Engineer for a cause other than those listed under Sub Clause 52.2 above, the Engineer shall decide whether the breach is fundamental or not.

  - Notwithstanding the above, the Employer may terminate the Contract for convenience.

  - If the Contract is terminated the Contractor shall stop work immediately, make the Site safe and secure and leave the Site as soon as reasonably possible.

- PAYMENT UPON TERMINATION

  - If the Contract is terminated because of a fundamental breach of Contract by the Contractor, the Engineer shall issue a certificate for the value of the work done up to the date of the issue of the certificate, less other recoveries due in terms of the contract, less taxes due to the deducted at source as per applicable law and less the percentage to apply to the work not  completed as indicated in the Contract Data.  Additional Liquidated Damages shall not apply.  If the total amount due to the Employer exceeds any payment due to the Contractor, the differences shall be a debt payable to the Employer.

  - If the Contract is terminated at the Employer’s convenience or because of a fundamental breach of contract by the Employer, the Engineer shall issue a certificate for the value of the work done, the reasonable cost of removal of Equipment, repatriation of the Contractor’s personnel employed solely on the works, and the Contractor’s costs of protecting and securing the Works and less advance payments received up to the date of the Certificate, less other recoveries due in terms of the contract and less taxes due to be deducted at source as per applicable law.

- PROPERTY

  - All materials on the Site, Plant, Equipment, Temporary Works and Works are deemed to be the property of the Employer, if the Contract is terminated because of a Contractor’s default.

- RELEASE FROM PERFORMANCE

55.1    If the Contract is frustrated by the outbreak of war or by another event entirely outside the control of either the Employer or the Contractor the Engineer shall certify that the Contract has been frustrated.  The Contractor shall make the Site safe and stop work as quickly as possible after receiving this certificate and shall be paid for all work carried out before receiving it and for any work carried out afterwards to which commitment was made.

- SUSPENSION OF LOAN OR CREDIT BY FINANCIER

  - In the event that the Financier suspends the Loan or Credit to the Employer, from which part of the payments to the Contractor are being made:

(a)	The Employer is obligated to notify the Contractor of such suspension within 7 days of having received the Financier’s suspension notice.

(b)	Under this condition the Employer will have the option of continuing the balance works or terminating of agreement.

F. SPECIAL CONDITIONS OF CONTRACT

- DESCRIPTION

The Contractor shall, at all times during the continuance of the contract, comply fully with all existing Acts, regulations and bye laws including all statutory amendments and reenactments of State or Central Government and other local authorities and any other enactments, notifications and acts that may be passed in future either by the State or the Central government or local authority, including Indian Workmen’s Compensation Act, 1923.  Contract Labour (Regulation and Abolition) Act 1970, the Child Labour Prohibition and Regulation Act 1986, and Equal Remuneration Act 1976, Factories Act, Minimum Wages Act 1948, Provident Fund Regulations, Employees Provident Fund Act 1952 EPF Act 1996 and related acts passed from time to time.  Schemes made under the Same Act the Buildings and other construction workers (Regulation of Employment and condition of Service) Act 1996, the Cess Act 1996 and also applicable Labour Regulations, Health and Sanitary Arrangement for Workmen, Insurance and other benefits and shall keep Employer indemnified in case any action is commenced by Competent authorities for contravention by the Contractor.

If the Employer is caused to pay or reimburse, such amounts as may be necessary to cause or observe, or for non-observance of the provisions stipulated above on the part of the Contractor, the Engineer shall have the right to deduct from any amounts due to the Contractor, his amount of Performance Security or recover from the Contractor personally any sum required or estimated to be required for making good the loss or damage suffered by the employer, responsibility in connection with the employees of the contractor, who shall, in no case, be treated as the employees of the Employer at any point of time.

1.1 A	RESPONSIBILITY FOR EXECUTION OF THE CONTRACT (CLAUSE 15 OF G.C.C.)

The Contractor shall carry out the entire work according to sound engineering practices.  The responsibility lies with the Contractor for the proper execution of the erection work according to existing laws and by laws at the time of contract execution.  The Contractor shall confirm in respects to the requirements to CEIG (Chief Electrical Inspector to Government) as and when required by them.  However, the Contractor shall have to follow the instructions of the Employer or his authorized representative in respect of the following.

- Progress reports to be submitted from time to time.

- Progress and completion of the work according to the time schedule.

- Execution of contract works to the Purchaser’s entire satisfaction.

- Submitting the details regarding the name of the responsible persons for execution of this contract.

- Preparing, submission and getting approval of the complete electrical system of the power plant including the switch yard from the CEIG will be contractor’s responsibility.

1.1. B.	NOTICES:

    - All Certificates, notices or written orders to be given by the Employer to the Contractor under the terms of the contract shall be served by sending by post to or delivering the same to Contractor’s principal place of business, or such other address as the Contractor shall nominate for this purpose.

    - All notices to be given to the TSSPDCL or to the Engineer under the terms of the Contract shall be served by sending by post or delivering the same to the respective addressee nominated for that purpose.

The Employer’s address is

Chief General Manager, Master Plan,

Southern Power Distribution Company of Telangana Limited,

Mint Compound,

Hyderabad - 500063.

The Engineer’s address is as given in the above CONTRACT DATA.

2.	WORKING HOURS

Before commencement of work, the contractor shall inform in writing, the normal working hours for his staff and workers. These hours be as far as possible in consonance with the Employer’s working hours for better coordination.

All the staff and workers should positively leave the site premises after these hours, except for authorized watch and ward personnel, approved by the employer.

- EXTRA SHIFT & OVERTIME WORK

At the commencement of work, the Contractor shall arrange for a general shift, as per working hours.

If, at a later date the employer feels that extra shift should be started to complete work allotted to the contractor within the time stipulated or to make up for any past delays.  The contractor shall arrange it.

- ACCIDENTS (CLAUSE 12 OF G.C.C.)

The employer will not be responsible for any damages or compensation payable inconsequence of an accident or injuries to any of the Contractor’s personnel or any third party.

The contractor shall insure at his cost-against any such eventuality as per rules in force and submit the documentary evidence of the Insurance Policy taken, positively prior to commencement of work at site and should keep policy valid by paying premium and other changes will handing over of the plant.

In case of any accidents at or near the site in connection with the execution of work, the contractor shall with in 24 hours, make a detailed report of accident and submit the same to the purchaser in the form provided by the purchaser.

The contractor shall also report such accidents to the competent authority as laid down by the existing rules and regulations and inform the Employer regarding the same.

Insurance coverage for all items shall be at the risk of the contractor.

5.	INDEMNITIES

5.1 	The contractor is liable for and indemnifies the TSSPDCL against losses, expenses and claims for loss or damage to physical property, personal injury and death caused by his own acts or omissions.

5.2	The contractor claiming indemnity is to take all reasonable steps to mitigate the lower damage will occur.

5.3	The contractor indemnifies the TSSPDCL against claims to damages caused by the movements of his equipment or temporary works.

  - The Contractor shall submit an “Indemnity Bond” to the TSSPDCL incorporating the above     points before taking up the execution of the work.

- LICENSE

The contractor shall have valid contractor’s license from the Electrical Inspector of the State, and he shall maintain its validity for the complete duration of the contract.

- TRANSPORT ARRANGEMENT

The contractor shall make the transport arrangement at his cost for his staff and workers to site.

- MACHINERY, TOOLS & TACKLES

The Contractor shall provide the required machinery/equipment, accessories, necessary tools and tackles, instruments, and all the normal consumable materials required for the satisfactory execution of this contract. The Contractor shall arrange for cranes for unloading and erection purpose, if required.

Gate Pass for Materials:

All tools, tackles, construction materials, welding materials etc., will be taken inside the site limits only after registration with security personnel.  Also any material will be taken out only on valid gate pass issued by purchaser’s representative after checking the proper “IN” gate passes.  The contractor shall have to preserve the “IN” gate passes obtained from security when every /any material is route inside the site to enable taking back the balance/excess materials, Tools and Tackles after completion of works.

- SAFETY PRECAUTIONS (CLAUSE 18 OF G.C.C.)

All the safety measures to avoid accidents shall be followed strictly in accordance with the safety rules and regulation laid down by the government authorities.

The Contractor shall take all safety precautions and shall provide proper scaffolding, life-belts, ladder, shock proof helmets & earth rods etc. to avoid accidents and to ensure safety, of not only his personnel but also the safety of the staff and workers of other contractors working at the same site.

The contractor shall take necessary precautions to ensure that no part of the building/structure damage or disfigured due to negligence on his part while carrying out the work.  In case of excess damage, the same shall be made good by the contractor immediately at his own cost.

Re-commissioning on energized equipment shall be carried out with proper safety permits issued by the Purchaser/Competent authorities. When required to work at heights or at hazardous location areas, the contractor shall carryout the same with utmost care and all safety precautions.

- FIRE PRECAUTIONS (CLAUSE 18 OF G.C.C.)

The contractor shall strictly instruct his site staff and workers to abide by the regulations in force at the site regarding all precautions to be taken to avoid fire hazards.

- WORKING AREA & CLEANLINESS

The Contractor shall keep the site of work in a clean and sanitary condition.  After the completion of the entire work, the contractor shall arrange to remove all the temporary structures, surplus materials, dirt, debris, etc. from the site and finished work shall be handed over the employer in a clean and complete shape.

- SITE DISCIPLINE

Strict discipline shall be observed by all the contractor’s personnel inside the premises of the site.  The contractor and his personnel shall abide by all the rules and regulations of the Employer, Disciplinary action shall be taken against the Contractor/his personnel and their services liable to be terminated, if found quarrelling/ violating the rules.

- SITE OFFICE & SITE STORES

The Contractor will make necessary arrangements for erection of his site office and site stores after getting written permission from the employer to erect such temporary structure at his own cost.  Temporary power supply will be provided at one point at the nearest switch room. The power consumption charges will have to be borne by the Contractor.  However, non-availability of the Crane does not leave the contractor off his responsibilities. The contractor is permitted to make use of water source available in any sub-station sites for construction purpose.

Transport of water from the source to the working areas will be contractor’s responsibility.

- APPROVAL OF INSTALLATION BY GOVERNMENT AUTHORITIES (CEIG)

Wherever approval of government authorities is required, as per existing rules and regulations, the Contractor shall obtain the same.

- MEASUREMENT (CLAUSE 39 OF G.C.C.)

The Engineer shall, except as otherwise stated ascertain and determine by measurement the value in terms of the contract of work done in accordance with the contract.  He shall, when required any part or parts of the works to be measured, give notice to the contractor’s authorized agent or representative, who shall forth with attend or send a qualified agent to assist the Engineer or the Engineer’s Representative in making such measurement, and shall furnish all particulars required by either of them.  Should the contractor not attend or neglect or omit to send such agent, then the measurement of the work.  For the purpose of measuring such permanent work as is to be measured by records and drawings, the Engineer’s representative shall prepare records and drawings month by month of such work and the contractor, as and when called upon to do so in writing, shall within fourteen days, attend to examine and agree such records and drawings, they shall be taken to be correct.  If, after examination of such records, and drawings, they shall nevertheless be taken to be correct, unless the contractor shall, within Fourteen days of such examination, lodge with the Engineer’s Representative, for decision by the Engineer, notice in writing of the respects in which such records and drawings are claimed by him to be incorrect.  Payments will be made to the contractor by cheque at monthly intervals.  The contractor shall submit his bills for work accomplished and measured by Engineer on or before the last day of month.

- INCOME TAX (CLAUSE 42 OF G.C.C.)

- Deductions will be made towards Income Tax at source by the TSSPDCL as directed by Income Tax Department.

b)	The Contractor’s staff, personnel and labour will be liable to pay personnel income taxes in India in respect of such of their salaries and wages as are chargeable under the laws and regulations for the time being in force, and the contractor shall perform such duties in regard to such deductions there of as may be imposed on him by such laws and regulations.

- TERMINATION OF CONTRACT FOR TSSPDCL CONVENIECE (CLAUSE 52 OF G.C.C.)

The TSSPDCL shall be entitled to terminate this contract at any time for the TSSPDCL convenience after giving 30 days prior notice to the contractor with a copy to the Engineer.

- LABOUR

The Contractor shall, unless otherwise provided in the contract, make his own arrangements, for the engagements of all staff and labour, local, or other, and for their payment, housing, feeding and transport.

The Contractor shall, if required by the Engineer, deliver to the Engineer a return in detail, in such form and at such intervals as the Engineer may prescribe showing the staff and the numbers of the several classes of labour from time to time employed by the Contractor on the Site and such information respecting Contractor’s Equipment as the Engineer may require.

- COMPLIANCE WITH LABOUR REGULATIONS

During continuance of the Contract, the Contractor shall abide at all times by all existing labour enactment’s and rules made there under, regulations, notifications and bye laws of the State or Central Government or local authority and any other labour law (including rules), regulations, bye laws that may be passed or notification that may be issued under any labour law in future either by the State or the Central Government or the local authority.  Salient features of some of the major labour laws that are applicable to construction industry are given below.  The Contractor shall keep the Employer indemnified in case any action is taken against the Employer by the competent authority on account of contravention of any of the provisions of any Act or rules made there under, regulations or notifications including amendments.  If the Employer is caused to pay or reimburse, such amounts as may be necessary to cause or observe, or for non-observance of the provisions stipulated in the notifications/bye laws/Acts/Rules /regulations including amendments, if any, on the part of the Contractor, the Engineer/Employer shall have the right to deduct any money due to the contractor including his amount of performance security.  The Employer/Engineer shall also have right to recover from the Contractor any sum required or estimated to be required for making good the loss or damage suffered by the Employer.

The employees of the Contractor in no case shall be treated as the employees of the Employer at any point of time.

SALIENT FEATURES OF SOME MAJOR LABOUR LAWS APPLICABLE TO ESTABLISHMENTS ENGAGED IN BUILDING AND OTHER CONSTRUTION WORK.

- Workmen Compensation Act 1923: - The Act provides for compensation in case of injury by accident arising out of and during the course of employment.

- Payment of Gratuity Act 1972: -  Gratuity is payable to an employee under the Act on satisfaction of certain conditions on separation if an employee has completed 5 years service or more or on death the rate of 15 days wages for every completed year of service.  The Act is applicable to all establishments employing 10 or more employees.

- Employees P. F. and Miscellaneous Provision Act 1952: The Act for monthly contributions by the employer plus workers @10% or 8.33%.  the benefits payable under the Act are:

- Pension or family pension retirement or death, as the case may be

Deposit linked insurance on the death in harness of the worker.

Payment of P.F. accumulation on retirement /death etc.

- Maternity Benefits Act 1951: -The Act provides for leave and some other benefits to women employees in case of confinement or miscarriage etc.

- Contract labour (Regulation &Abolition) Act 1970: - The Act provides for certain welfare measures to be provided b y the contractor to contract labour and in case the Contractor fails to provide, the same are required to be provided, by the principal Employer by Law.  The Principal Employer is required to take Certificate of Registration and the Contractor is required to take license from the designated officer.  The Act is applicable to the establishments or Contractor of Principal Employer if they employ 20 or more contract labour.

- Minimum Wages Act 1948: - The Employer is supposed to pay not less than the Minimum Wages fixed by appropriate Government as per provision of the Act if the employment is a scheduled employment.  Constructions of Buildings, Roads and Runways are scheduled employments.

- Payment of Wages Act 1936: - It lays down as to by what date the wages are to be paid, when it will be paid and what deductions can be made from the wages of the workers.

- Equal Remuneration Act 1979: - The Act provides for payment of equal wages for work of equal nature to Male and Female workers and for not making discrimination against Female employees in the matters of transfers, training and promotions etc.

- Payment of Bonus Act 1965: - The Act is applicable to all establishments employing 20 or more employees. The Act provides for payments of annual bonus subject to a minimum of 8.33% of wages and maximum of 20% of wages to employees drawing Rs.3500/- per month or less.  The bonus to be paid to employees getting Rs.2500/- per month or above up to Rs.3500/- per month shall be worked out by taking wages as Rs.2500/- per month only.   The Act does not apply to certain establishments.  The newly set-up establishments are exempted for five years in certain circumstances.  Some of the State Governments have reduced the employment size from 20 to 10 for the purpose of applicability of this Act.

- Industrial Disputes Act 1947: - The Act lays down the machinery and procedure for resolution of Industrial disputes, in what situations or lock-out becomes illegal and what are the requirements of laying off or retrenching the employees or closing down the establishments.

- Industrial Employment (Standing Orders) Act 1946: - It is applicable to all establishments employing 100 or more workmen (employment size reduced by some of the States and Central government to 50).  The Act provides for laying down rules governing the conditions of employment by the Employment on matters provided in the Act and get the same certified by the designated Authority.

- Trade Union Act 1926: - The Act lays down the procedure for registration of trade unions of workmen and employers.  The Trade Unions registered under the Act have been given certain immunities from civil and criminal liabilities.

m)	Child Labour (prohibition & Regulation) Act 1986: - The Act prohibits employment of children below 14 years of age in certain occupations and process and provides for regulation of employment of children in all other occupations and processes. Employment of Child Labour is prohibited in Building and Construction Industry.

n)	Inter-State Migrant Workmen’s (Regulation of Employment & Conditions of Service) Act 1979:- The Act is applicable to an establishment which employs 5 or more inter-state migrant workmen through an intermediary (who has recruited workmen in one state for employment in the establishment situated in another state).  The Inter State migrant workmen, in an establishment to which this Act becomes applicable, are required to be provided certain facilities such as housing, medical aid, traveling expenses from home up to the establishment and back, etc.

o)	The Building and Other Construction Workers (Regulation of Employment and Conditions of Service) Act 1996 and the Cess Act of 1996:  All the establishments who carry on any building or other construction work and employ 10 or more workers are covered under this Act.  All such establishments are required to pay cess at the rate not exceeding 2% of the cost of construction as may be modified by the Government.  The Employer of the establishment is required to provide safety measures at the building or construction work and other welfare measures, such as Canteens, First- Aid facilities, Ambulance, Housing accommodations for workers near the work place etc.  The Employer to whom the Act applies has to obtain a registration certificate from the Registering Officer appointed by the Government.

p)	Factories Act 1948: - The Act lays down the procedure for approval at plans before setting up a factory, health and safety provisions, welfare provisions, working hours, annual earned leave and rendering information regarding accidents or dangerous occurrences to designated authorities.  It is applicable to premises employing 10 persons or more with aid of power or 20 or more persons without the aid of power engaged in manufacturing process.

- ARBITRATION (GCC CLAUSE 24.1)

The Procedure for arbitration will be as laid down Indian Arbitration and conciliation act 1996.

- Responsibility for execution of the Contract:

The contractor shall carryout the entire work according to sound Engineering practices. The responsibility lies with the contractor for proper execution of work according to existing laws and bylaws. The contractor shall have to follow the instructions of the Employer or Engineer – In – Charge.

a)	Progress reports shall be furnished fortnightly.

b)	The details of project manager and site supervisors.

c)	Inspection of supports, conductor and other equipment at manufacturer’s site by the Employer.

d)	Approval test certificates before dispatch the material /equipment to site.

e)          Proper storage of material / equipment.

f)	“As Built” drawings and schedules shall be submitted with in 15 days of completion of the work.

- Operating manuals and operating instructions shall be furnished.

22.  	All the statutory clearances required for execution of works from various agency will be made available to the Bidder by TSSPDCL.

SECTION – 5

TECHNICAL SPECIFICATIONS

A.CIVIL TECHINCAL SPECIFICATION

A.CIVIL TECHINCAL SPECIFICATION

General :-

The Specification for various works should conform to the relevant clauses of the APSS and the special specifications included in the tender schedule. If there is any difference between the two, the later will be applicable. If for any item of work, detailed specifications are not indicated either in these technical specifications or in the APSS then, that work shall be carried out as per the relevant Indian Standard specifications (latest edition).

a.    The scope of work includes Construction of Construction of Compound Wall for newly allotted land of Uppal Bhagayat Phase-II layout, for proposed of new 33/11KV Sub-Station in Habsiguda Circle, Master Plan RR Circle of Master plan Zone (Reserved under Waddera/Sagara category)

Type of Construction:-

b. The building is proposed to be constructed using RCC framed structure               (multistoried). The superstructure will be with brick masonry of 230mm thick or as per approved drawings and as directed by Engineer in charge.

1.  TENDER DRAWINGS:

a)  	The following tender drawings for civil works are attached with the Bid document to give the idea of nature of work to Bidders.

b)	Tender drawings attached are preliminary and meant for Bid purpose only. They shall not be considered as final drawings.

IS- STANDARD:

The civil works shall be in general conform to the following standards: -

IS: 269	Specification for ordinary rapid hardening and low heat Portland cement.

IS: 383 	Specification for coarse and fine aggregate from natural sources for concrete.

IS: 1199 	Method of sampling and analysis of concrete.

IS: 3025 	Method of sampling and test (physical and chemical water used in industry).

IS: 456 	Code of practice for plain and reinforced concrete (latest revision).

IS: 432 	Specification for mild steel and medium tensile steel bars and hard drawn steel wire for concrete reinforcement (part-I & II).

IS: 1139 	Specification for hot rolled mild steel and medium tensile steel deformed bars for concrete reinforcement.

IS: 1566 	Specification for plain and hard drawn steel wire fabricator concrete reinforcement.

IS: 1785 	Specification for plain and hard drawn steel wire for pre-stressed concrete (part-II).

IS: 1786 	Specification for cold twisted steel bars for concrete reinforcement.

IS: 2090 	Specification for high tensile steel bars used in pre-stressed concrete.

IS: 4990 	Specification for plywood for concrete shuttering work.

IS: 2645 	Specification or integral cement water proofing compounds.

IS: 4461 	Cold worked steel bars for the reinforcement of concrete.

IS: 2514	 Specification for concrete vibrating tables.

IS: 802 	 Code of practice for the design and construction of transmission line           towers (part-I, II & III).

IS: 200 	Method of measurement of building and civil engineering (part-I) work: part-I: Earthwork.

IS: 3764	 Safety code for excavation work.

IS: 4701	 Code of practice for earthwork on canals.

IS: 2502 	Code of practice for bending and fixing of bars for concrete reinforcement.

IS: 1838 	Performed fillers for expansion joints concrete non-extruding and resilient type (bitumen impregnated filler).

IS: 2386 	Specific gravity, density, voids, absorption and (part-III) buckling.

IS: 2505 	General requirements for concrete vibrators, immersion type.

IS: 2506 	Screen board concrete vibrators.

IS: 3370 	Code of practice for concrete structures for the storage of liquids.

IS: 3350	 Methods of tests for routine control for water used in industry.

IS: 4456 	Form vibrators for concrete.

IS: 9103 	Admixtures for concrete.

IS: 517 	Methods of test for strength of concrete.

IS: 4091 	Code of practice for the design and construction of foundation for transmission lines.

IS: 1893 	Code of practice for seismic loads and designs.

IS: 800 	Code of practice for structural steel is building.

Note:  The APSS is available on sale at government of A.P, printing press.

2.0    LEVELLING OF SITE: -

The site is to be levelled all-round the building area including removal of vegetation. The Ground also shall be lowered or raised to the required level if necessary with excavated earth or as directed by Engineer at site.

3.0       EXCAVATION: -

Excavation shall include careful removal of all materials of whatever nature and whether dry or wet, necessary for the construction of work, and leveling site exactly in accordance with lines, levels, grades and curves shown in the plans or as directed by the Engineer-in-charge. It shall be taken to exact widths and levels of the lowest step of foundation /footing/floor and the sides shall be left to plumb where the nature of the soil permits. Any shoring, strutting and timbering or cutting of extra widths of trenches required for providing working space shall be done by the contractor and the same shall be deemed to have been included in the quoted rate. The contractor shall notify the Engineer-in-charge before starting excavation and take cross section levels (for purposes of measurements) jointly with the Engineer-in-charge before the Ground is disturbed. The bottom of the foundation shall be leveled both longitudinally and transversely stepped as directed, the contractor shall provide suitable arrangements to prevent surface water from any source entering the foundation pits at his own cost.

No blasting shall be permitted for excavation of foundations without prior permission of the Engineer-in-charge. The contractor shall not undertake any concreting in foundation until the excavation pit is approved by the Engineer-in-charge. The rate quoted for excavation shall include bailing or pumping of water which may accumulate in the excavation during the process of work either from seepage, rain or any other cause. The excavation shall be kept away from water. All materials excavated from the foundation of whatever kind they shall be placed at a distance of more than 1.5M from the edge of the foundation or as directed by the Engineer-in-charge. All excavated material shall remain the properties of the TSSPDCL. Material suitable for filling or other use shall be stacked in places as directed by Engineer-in-charge.

Surplus earth and soil which are not useful shall be removed and conveyed as directed by Engineer-in-charge.

The quoted rate shall include clearing of site, setting out and works required for excavation, cost of excavation, pumping and bailing out rain water/surface water accumulated in the excavated pit, stacking of excavated earth, shoring, removal and disposal of surplus excavated soil from the construction site if any, with initial leads and lifts, labour charges, including hire charges of machinery ,tools& plants ,insurance, all incidental charges etc. complete for finished item of work as directed by Engineer-in-charge.

4.0      ANTI-TERMITE TREATMENT:-

SCOPE: The scope of work is to set up a chemical barrier against attack by subterranean termites.

GENERAL: All work shall in general, be executed as specified in IS:6313 Part-II,IS:6333 Part II,IS:6433:1978,IS 2682:1984 and as per approved specification of the agency having special know-how for the job.  All necessary work to ensure uniform distribution and proper penetration of treating solution shall be done according to the instruction of the Engineer-in-charge.  Soil treatment shall not be done when it is raining or when the soil is wet with rain or subsoil water.  Once formed, the treated soil barrier shall not be disturbed.

CHEMICALS AND RATE OF APPLICATION:

Any of the following chemicals (conforming to relevant Indian Standards) in water emulsion shall be applied by pressure pumps uniformly over the area treated:-

Chemicals                     	 Concentration by weight percent.

Dieldrin (IS:1052-1962)                     			0.5

Aldrin   (IS:1306-1958)                     			0.5

Chlordane (IS:2863-1964)				1.0

Heptachlor						0.5

ACCEPTANCE CRITERIA:  The contractor shall give a 1 year service guarantee in writing supplemented by a separate and unilateral guarantee from the specialized agency for the job to keep the building treated free of termites for the specified period at no extra cost to the purchaser.

I.S. CODE: Relevant code applicable for this specification:  IS:6317(Part-II)-1971: Code of practice for Anti-termite Measures in buildings.

5.0       FOUNDATIONS

CC (1:4:8) using 40mm HBG metal shall be laid as leveling course under footings UG sump, storm water drain, septic tank. The CC work shall be executed as per specification numbers 402 of APSS.

The quoted rate shall include cost of all materials, all operations, labour charges, tools, tackles, machinery, curing, dewatering, water leads ,all leads and lifts and the incidental charges connected with the work etc. complete for finished item of work as directed by the Engineer-in-charge.

6.0       CRS MASONRY FOR FOUNDATIONS AND BASEMENT:-

The foundations and basement at stilt floor rooms and Retaining wall shall be constructed with CRS. masonry using hard broken granite stones in CM (1:6).

The quoted rate shall include cost of all materials, all operations, including dewatering if required, labour charges tools, tackles, machinery, curing, water leads, all leads and lifts and other incidental charges connected with the work etc. complete for finished item of work and as directed by the Engineer-in-charge.

a)	SCOPE:  The contractor shall furnish all labour, materials and equipment required for the construction of all stone masonry work required as mentioned in this section as per drawings and specifications.

b)	MATERIALS:  Stones shall be obtained from the quarries to be approved by the engineer and shall conform to IS:1597 (Part-I).  Stones shall be of uniform colour and texture, hard, durable, tough, and the best quality of its respective kind. These shall be free from decay, sand holes, veins, flaws cracks and other defects.  These shall be carried to such a way as to be most suitable for one particular class of work for which these are required.  Stone not suited for the particular class of work removed from the site be the contractor.

c)	LAYING:

The stones shall be laid on their broadest face.

Stratified stones shall be laid on their natural bed i.e., with the strata perpendicular to the pressure.  The course shall be built perpendicular to the pressure. Where there is to be variation in the depth of courses, larger stones are to be placed in the lower courses, the thickness of courses decreasing gradually towards the top of the wall. To give sufficient lateral bond, a stone in any course should overlap the stone in the course below i.e., joints parallel to the pressure in two adjoining courses should not lie too closely in the same vertical line To give sufficient transverse bond, the prescribed number of headers must extend from front to back of thin walls or from outside to the interior of thick walls. At all angle junctions of walls, the stones at each alternative course shall be so carried into each of the respective walls as   to unite the work thoroughly. Where breaks are unavoidable in carrying up the    continuously in horizontal courses, sufficient long steps  shall be left to join the old and new work. If it is necessary to move a stone after it has been placed on the mortar bed, it should be lifted clear and rest and not made   to slide over stones already laid.

d)	WATERING:

To prevent absorption of water from the mortar, the stones shall be sufficiently well wetted before laying. All masonry shall be kept watered for three weeks from the date of building in place unless otherwise instructed by the engineer. At the close of the day's work or for other period of cessation of the work, the top of all unfinished masonry is to be kept well flooded. Should the mortar perish ie., become dry, white or powder through neglect of watering the work shall be pulled   and rebuilt at the contractor's expense. All masonry shall be washed down on completion of all stains. Mortar and Materials to Conform to Standard Specification : The mortar to be used for each class of masonry shall conform to the particular standard specification for that class of mortar and the standard specification for the materials used.]

7.0	REFILLING THE FOUNDATIONS & BASEMENT :

Refilling the foundations & basement is to be done with useful available sand/excavated soils and as directed by the Engineer-in-charge.

Filling shall be done after the concrete or masonry in the foundation has fully set and its curing is completed. It shall be done in such a manner as not to cause undue thrust/impact on any part of the structure.

Back filling around completed foundations shall be done to the required lines and levels/depths including any trimming of surfaces as may be necessary. This will be done with selected and approved excavated useful soil as directed by Engineer-in-charge. The refilling shall be done in horizontal layers of thickness not exceeding 15cm, free from pockets with careful watering, ramming and rolling etc. to obtain necessary level of compaction.

The contractor shall not fill in and around any work until it has been approved by Engineer-in-charge.

The quoted rate shall include cost of excavated useful soil, carrying up to directed locations, placing, watering, compacting in layers, trimming and dressing to finished surface and disposal of surplus material if any.

8.0        BRICK MASONRY:

The superstructure of the building shall be constructed in all thickness with brick masonry in CM (1:6) using second class bricks of approved quality from approved source having minimum crushing strength of 40 kg/cm2 and water absorption not exceeding 20   % by weight.

a)	Scope:

The contractor shall  furnish  all  labour,  materials  and  equipment  required  for  the  construction  for  all brick masonry work as shown in the construction drawings.

b)         Bricks:

Light weight bricks conforming to IS code shall be of uniform  colour, strength and size with  minimum crushing strength  of   kg/cm².  The bricks shall have smooth surfaces with  corners straight; they  shall  not  be twisted  or  chipped;    when broken they shall reveal a fine, uniform, no vitreous grain; they shall emit ringing  sound when  tapped  with  a  hammer;  they  shall absorb water on immersion (not more than  one sixth of its  original  weight after  soaking for 15   minutes) and dry sufficiently quickly. The bricks shall not show any sign of  efflorescence  after soaking and  drying  in shade.  If the bricks show any sort of efflorescence the  contractor  shall  do  the  necessary treatment  at  his  own cost  to  the  satisfaction of the  engineer.

All bricks shall be subjected to  inspection  and  approval  and   representative  samples  shall  be  submitted  before  ordering out.    Contractor shall submit sample of bricks and arrange to test these bricks in approved laboratory and submit the test results for approval prior to commencement of work.

c)	Mortar:

Mortar shall be prepared with the materials as specified in  this specification and the mortar shall conform to IS:2250.  The  type  of  mortar  to  be  used  shall be in proportion  specified in Schedule -'A'.

d)      	Brick Works:

Soaking of Bricks :

Bricks required for  masonry  in  cement  mortar  shall  be  wetted  to  saturation  point  by  prolonged immersion, but  never by spraying.  The  cessation  of  bubbles,  when  the  bricks  are  immersed  in  water, shall be an indication of thorough soaking of bricks.  The  soaked  bricks  shall  be  kept on wooden plank to avoid earth being smeared on them.

e)     	Laying:

Brick  work  shall be laid with best skill and the greatest care and diligence. Each brick  shall  be  pressed  on  the  layer  of  the  specified  mortar  so that this spreads all  around it and fill the joints which  shall  never  be  more  than 10  mm  nor  less  than 5 mm wide.  Mortar ingredients  shall be of proper grain size to permit joints within these  limits.

The whole of the brick work shall be built in English  bond unless otherwise  directed.    No  four brick courses shall  rise more than 25 mm over above the  same  laid  dry.    No  brick bats shall be used excess where required as closures The  bricks  shall  be  thoroughly  bedded on cement mortar during each layer.  After every third course reinforcing steel consisting of 2Nos. of 6mm dia mild steel bars shall be provided and these shall be anchored to the structural steel as directed by the Engineer.  However, the reinforcement steel shall be separately paid for at their quoted rates for reinforcement.

The work will be done in  a  proper  manner  in  the  first instance  only  and no grouting shall be resorted to. String courses, cornices  and  mouldings shall  not  generally  be  provided  unless as shown on the drawings or as directed by the engineer.  The architectural features and treatment  if  required  as per the drawings or as may be finalized before execution  and  such  items  whether  in  large  or   small  quantities  and  any  shape  and  size,  shall  have  to be  provided by the contractor at the rates in  relevant  items  of the  bill  of  quantities.   The contractor shall not be eligible to claim any extra rate  on  this  account.    The   brick  work  must  be  laid  true  to  line  and level with  horizontal courses and  vertical  perpendicular  faces  and  corners etc.

f)       	Non-Bearing Walls:

Non-bearing walls (dividing walls) shall be built of choice  bricks, for  both  header and stretcher courses.  No broken bricks or bricks with chipped corners will be accepted.

g)       	Curing:

Green  work  shall  be  protected  from  rain  by  suitable covering.   Brick  work  in  cement  mortar  shall  be kept constantly moist on all the faces for a minimum  period  of ten (10)  days.    The  top  of  masonry work shall be left  flooded at the close of the day.

h)   	Measurements:

Masonry  work in general shall be geometrically measured by volume .  The volume of the walls shall be reduced for  all voids,  hollows,  recess and openings of net area more than  half a square meter,  without accounting for  flares,  that   is  discounting  only  the volume obtained multiplying the net span of the opening in rough by thickness of  the  wall the depth of the recess, assuming that the volume of flares and splays shall cover the higher skill required  in  their  construction.    The  provision, during  construction  of recess  and  holes for passage of pipes as designed  and   previously  arranged  and  ordered, shall not  entitle the   contractor to any compensation.  The plinth level shall be  taken as 0.00 level of the respective  building. The unit rate   shall include supply of materials, transport, mortar of required proportion and curing.

All  the  measurements  are  to  be  done  as  per  IS:1200 (relevant parts) for the items not covered above.

Contractor shall submit sample of bricks and arrange to test these bricks in approved laboratory and submit the test results for approval prior to commencement of work .

Bricks required for masonry in cement mortar shall be thoroughly soaked in clean water before use for at least six hours and until air bubbles ceases to come out. The soaked bricks shall be kept on wooden plank or brick platform to avoid earth being smeared on them.

Only skilled and experienced masons shall be employed for laying the brick masonry. Brick work shall be laid in English bond unless otherwise specified. Half or cut bricks shall not be used except as closures when needed to complete the bond. Each course shall be perfectly straight horizontally and transversely. The walls shall be taken up truly plumb. The level of the brickwork in vertical walls shall be checked up every one meter interval.

All iron fixtures, pipes, conduits, drain sleeves, bolts, hold fasts of doors and windows etc. which are required to be built in wall shall be embedded in cement mortar or in cement concrete as specified, in their correct position, as the work proceeds.

Brick masonry shall be in CM (1:4) for partitions in rooms.

The quoted rate shall include the supply of all materials, including conveyance seigniorage charges labour, tools, tackle, plant and equipment, scaffolding, shuttering, pocking the concrete and temporary works, curing with all leads and lifts and all other incidental charges required to complete the work in accordance with the standard specification. No deductions shall be made for openings less than 0.1 m²  in area and for fixtures up to 0.05 m² in area.

i)   	Applicable Codes and Specifications:

The following codes, standards and specifications are made a part of  this  specification,  All  standards,  tentative specifications,  specifications, codes of practice referred  to  herein  shall  be  the  latest  edition  including  all applicable official amendments and revisions.

In case of discrepancy between this specification and those referred to herein, this specification shall govern.

IS : 1077   	:   	Common burnt clay building bricks

IS : 3102   	:   	Classification of burnt clay bricks

IS : 2180  	 :   	Burnt clay building bricks - heavy duty

IS : 3495   	:   	Method of sampling and testing clay  building bricks

IS : 2691   	:   	Burnt clay facing bricks

IS : 2212  	 :  	 Code of practice for brick work

9.  PLAIN AND REINFORCED CEMENT CONCRETE WORKS :

9.1     SCOPE :

This section  of the specification covers the technical requirements for  forming, placing and finishing of concrete, plain and reinforced cement concrete for all structures and their foundations at all levels and elevations e.g. buildings, walls, cable tunnels, cable ducts,  foundations and footings, pits, posts, drains,  water tanks as per approved drawings, manholes, etc., as required to complete the job as per the approved drawings.  All concrete works as indicated in the scope of this contract shall be carried out as per these specifications.

a)	This specification shall also apply to the extent it has been referred to or applicable with the special requirements of structures covered in scope of IS: 456. IS: 456 shall form a part of these specifications and shall be complied with unless permitted otherwise. For any particular aspect not covered by these code, appropriate IS code, specifications and/or replacement by any International Code of practice as may be specified by the Engineer shall be followed. All codes and Standards shall conform to its latest revisions.

b)	Nominal Mix and Design mix :

1:2:4, 1:3:6 and 1:4:8 shall be of Nominal Mix , M20 and above shall be of Design Mix.  The mix proportions for all grades of concrete shall be designed to obtain strengths for respective grades of concrete.  Preliminary tests as specified in the IS: 456 and required by the purchaser, shall be carried out sufficiently ahead of the actual commencement of the work with different grades of concrete made from representative samples of aggregates and cement expected to be used on the job to ascertain the ratios by weight of cement to total quantities of fine and coarse aggregate and the water cement ratio required to produce a concrete of specified strength and desired workability.

The contractor at his cost at an approved testing laboratory shall carry out the mix designs.

Whenever the sources of fine and course aggregates and/or brand of cement is changed, the tests shall again be carried out on the materials for ascertaining their suitability and the Mix Design shall also be carried out and this mix shall be used subject to the approval of the Executive Engineer.

The cement @ 350 kg/m³ of M20 grade concrete is considered for the estimate of this work. Tenderers are required to quote their rates keeping in view of the cement quantity as above.  However, the actual utilization of cement will be as per the design mix.  Excess/Less usage than the provision of 350 kg will be either reimbursed or recovered @ Rs.        /- per M.T irrespective of other ingredients.

9.2	GENERAL REQUIREMENTS:

9.2.1 	WORK TO BE PROVIDED BY THE CONTRACTOR:

The work to be provided for by the Contractor, unless otherwise specified shall include but not be limited to the following:

  - Furnish all labour, supervision, services including facilities as may be required under statutory labour regulations, materials, forms, templates, supports, scaffolds, approaches, aids, construction equipment, tools and plants, transportations, etc. required for the completion of work as per approved drawings.

  - Except where it is excluded from the Scope of Contract, Contractor shall prepare progressively and submit for approval detailed drawings and Bar Bending Schedules for reinforcement bars showing the positions and details of spacers, supports, chairs, hangers etc.

  - Design and prepare working drawings of formworks, scaffolds, supports, etc. and submit for approval.

  - Submit for approval shop drawings for various inserts, anchors, anchor bolts, pipe sleeves, embedment, hangers, openings, frames etc.

  - Submit for approval detailed drawings of supports, templates, hangers, etc. required for installation of various embedments like inserts, anchor bolts, pipe sleeves, frames, joint seals, frames, openings etc.

  - Submit for approval detailed schemes of all operations required for executing the work, e.g. Material handling, Concrete mixing, placement of concrete, compaction, curing, services, approaches, etc.

  - Design and submit for approval concrete mix designs required to be adopted on the job.

  - Furnish samples and submit for approval results of tests of various properties of the following:

i) 	The various ingredients of concrete

ii) 	Concrete

iii) 	Embedment

iv) 	Joint seals

  - Provide all incidental items not shown or specified in particular but reasonably implied or necessary for successful completion of the work in accordance with the drawings, specifications and schedule of items.

  - For supply of certain materials normally manufactured by specialist firms, the contractor may have to produce, if directed by the Engineer, a guarantee in approved pro forma for satisfactory performance for one year as may be specified, binding both the manufacturers and the contractor, jointly and severally.

- SAMPLES:

Samples of the following materials and any other materials proposed to be used, shall be submitted as directed by the Engineer, in sufficient quantities free of cost, for approval. Approved samples will be preserved by the Engineer for future reference. The approval of the Engineer shall not, in any way, relieve the contractor of his responsibility of supplying materials of specified qualities:

i)	         Coarse and fine aggregates.

ii)         Admixtures.

    - Plywood for formwork.

- DESIGN MIX:

Design mix as per Clauses 11.2.1 (g) of this specification giving proportions of the ingredients, sources of aggregates and cement, along with accompanying test results of trial mixes as per relevant I.S., is to be submitted to the Engineer for his approval before it can be used on the works.

- Detailed Drawings and Bar Bending Schedules:

Detailed working drawings and Bar Bending Schedules in accordance with this specification.

- Inspection Reports: Inspection Reports in respect of formwork and reinforcement and any other item of work as may be desired by the Engineer in accordance with Clause 11.2.4 of this specification.

- Test Reports: Reports of tests of various materials and concrete as required under Clause 21.0 SAMPLING & TESTING of this specification.

- Any other data that may be required as per this specification.

    - MATERIALS :

a)	Cement:

Cement shall conform to IS: 269.  The contractor shall be fully satisfied with the   quality and properties of cement used irrespective of its source and/or supply.

b)	Admixtures:

All concrete shall be designed for normal rate of setting and hardening at normal temperature. Variations in temperature and humidity under different climatic conditions will affect the rate of setting and hardening, which will, in turn, affect the workability and quality of the concrete. Admixtures may be permitted to be used in accordance with IS:456 to modify the rate of hardening , to improve workability or as an aid to control concrete quality.

The  Executive  Engineer  shall  have  the authority at any time, and from time to time to order the  addition  of  any  air  entering  agent  or  other  admixtures,  to any mix of  concrete in such proportionate quantity or mode, as he  may specify and the contractor shall comply with the same without any extra cost.

c)	Aggregates:

All the aggregates shall conform to IS:383.  The natural aggregates  shall  be  chemically  inert,   strong,   hard, durable,  of limited porosity, free from adherent coatings,  clay lumps, coal and coal residues  and  shall  contain  no   organic  or  other  admixtures  that may cause corrosion of  reinforcement  or  impair  the  strength or durability of  concrete.  The limits of the content of deleterious materials in aggregate are indicated below.

Limits of the content of Deleterious Materials

(Percent by weight of aggregate)

Deleterious                     	      	Fine aggregates                   Coarse aggregates

Substances                      	      --------------------------            -----------------------------

Crushed   	Uncrushed         Crushed  	Uncrushed

Coal & lignite                     1.00           	1.00              	  1.00     	    1.00

Clay lumps                          1.00          	1.00             	  1.00        	    1.00

Soft fragments                        -               	   -                   	  3.00                      -

Material passing                  3.00          	3.00                	  3.00         	    3.00

75 micron IS sieve

Shale                                    1.00                  -                          -                         -

Approved natural sand  and  crushed  stone  for  structural concrete  and  well  washed,  thoroughly cleaned and graded natural gravel, for  lean  and backfill cement   concrete  shall be used as aggregate.  Representative samples of selected aggregates shall be  tested  at  the  contractor's cost for sieve analysis from time to time as required by the engineer for  approval.

i)	Fine Aggregates:

Fine  aggregate  (sand)  shall be clean, sharp, coarse sand with a fineness  modules  between  2.2  and  3.2  (fineness  modulus  is  the  sum of cumulative percentages retained on  the IS sieves given below for gradation  divided  by  100).  The  contractor shall check and ensure that local sand will satisfy this requirement and if necessary shall include for and supply materials from other sources which  comply  with  the specifications, it shall be graded as follows.

IS sieve                               	P e r c e n t a g e   p a s s i n g   f o r

designation                	 Grading     		Grading   	Grading

Zone -I        		 Zone - II    	Zone -III

10 mm                 	100             		100        	  100

4.75 mm               	90-100          		90-100     	  90-100

2.36 mm               	60-95           		75-100       	  85-100

IS sieve                               	P e r c e n t a g e   p a s s i n g   f o r

designation                	 Grading     		Grading   	Grading

Zone -I        		 Zone - II    	Zone -III

1.18 mm               	30-70           		55-90      	  75-100

600 microns           	15-34           		35-59     	   60-79

300 microns           	5-20           		 8-30       	  12-40

150 microns           	0-10        		 0-10       	  0-10

The objectionable foreign matter in sand shall  be  removed by screening or washing or both as required.

ii) Coarse Aggregate: The coarse aggregate (crushed stone) shall conform to the following grading limits.

Grading Limits:

IS sieve                        Percentage retained for grade aggregate

designation                40 mm          20 mm       	17 mm                 12.5 mm

80 mm                       -         	   -        	    -         	        -

40 mm                       0-5        	  0             	  0        	       0

20 mm                       30-70          0-5        	  0          	       0

17 mm                       -          	  -         	  0-10       	       -

12.5 mm                     -          	   -       	    	  -          	    0-10

10 mm                       65-90         45-75       	30-70      	   15-60

4.75 mm                    95-100       90-100      	90-100     	   90-100

The  pieces  shall  be  angular  in  shape  and  shall have  granular or  crystalline  surfaces.    Friable,  flaky  and laminated pieces, mica and shale, if present, shall be only  in  such  quantities  that  will  not,  in  the  opinion of engineer, affect adversely the strength and durability of concrete.  The maximum size of the aggregate shall be as specified in the drawings/specifications.  The maximum size  of  coarse  aggregate

shall be the maximum size specified,  but in no case greater than 1/4 of the minimum thickness of the member provided that the concrete can be placed without difficulty so as to surround all  reinforcement  throughout  and fill  the  corners of the form.  For heavily reinforced concrete members, the nominal maximum size of the aggregate  shall be 5 mm less than the minimum clear distance  between  the  reinforcing  main  bars  or 5 mm less than the minimum  cover to the reinforcement whichever is smaller.

Crushing Value:

The aggregate crushing value, when determined in accordance with IS:2386 (Part IV) shall not  exceed  forty  five  (45)  percent  for  aggregate  used  for  concrete other than for wearing surfaces and thirty (30) percent for  concrete  for wearing   surfaces,  such  as  roads,  pavements  and  floor  finishes.

Impact Value:

As an  alternative  the  aggregate  impact  value  may  be determined  in  accordance  with  the  methods specified in IS:2386 (Part IV).  The impact value shall not exceed forty five (45) percent by weight for aggregate used for concrete other than for wearing surfaces and thirty (30) percent  by  weight  for concrete  for  wearing surfaces, such as roads,  pavements and floor finishes.

Abrasion Value:

Unless otherwise agreed to between the  purchaser  and  the supplier,  the abrasion value of aggregates, when tested in accordance with the method specified in IS:2386 (Part  IV),   using  Los  Angeles Machine, shall not exceed the following  values :

A.      For aggregates to be used in         Thirty (30)

concrete for wearing surfaces          percent

B.      For aggregate to be used in          Fifty (50)

other concrete (structural)              percent

The amount of fine particles occurring in the free state or as loose adherents shall not exceed 1% when  determined  by laboratory sedimentation  tests  as  per IS:2386.  After 24 hours immersion in water, a previously dried  sample  shall not  have  gained  more  than 10% of its even dry weight in air, as determined by IS:2386.   Should  at  any  time  the engineer have reason to consider any aggregate defective or of poor quality, then irrespective of any previous approval or tests, representative samples of such materials shall be   immediately tested and until  the  results  of  such  tests prove the material to be satisfactory, it shall not be used for any  work.  The contractor shall not be entitled to any  claim of any nature on this account.   The  cost  of  these tests  (including collection of samples and transportation) shall be borne by the contractor.

d)	Reinforcing Steel:

Reinforcement shall consist of any of the  following  types but shall conform to requirements shown on the drawings and   should be corrosion resistant.

-    Plain mild steel bars, Grade I (IS:432 Part I & IS:226)

-    Cold twisted or deformed bars (IS:1786) Grade Fe 415

-    Mild steel and medium tensile steel deformed bars (IS:1139)

-    Medium tensile steel bars (IS:432 Part I & IS:961)

-    Hard drawn steel wire mesh, fabric (IS:1566 & IS:432 Part II)

-    Structural steel sections and plates shall conform IS : 226 and IS : 2062.

i)		All  steel  shall be of grade I quality unless specifically permitted by the engineer. No rerolled scrap  steel  bars,  pitted or  otherwise  defective  bars  shall  be used.  The  contractor  shall  check  and   ensure   that   appropriate reinforcement bars  are  used  for  the  work.    Otherwise necessary tests shall be made by the contractor at his  own cost  to  ensure  that  quality  and physical properties of  materials used,  conform  to  the   specifications.      No  complaints or claims shall be entertained on this account.

ii)	All  reinforcing materials, before their final use shall be  free from loose mill scale, rust, dust, oily or  bituminous  coating or any other injurious adherents.

iii)	Pitted  and  otherwise  defective  bars  and rerolled scrap steel bars shall not be used.

The contractor shall procure in time as necessary and check measure  the  reinforcing  materials   required   for   the continuous  scheduled progress of work till the completion.

iv)	The reinforcement shall not be  placed  in  direct  contact with  the  Ground  but  stacked  on timber sleepers or such similar arrangement.  The  reinforcement  shall  be  coated with  cement  slurry  before  stacking to prevent scale and rust.  Fabricated reinforcement shall be  carefully  stored to prevent damage, distortion, corrosion and deterioration.

v) 	Welding may be permitted with the written approval  of  the  engineer, provided the carbon content of steel used is less than 0.3  per  cent.    Welding  so  permitted  shall be in accordance with IS:317.  Tack welding of reinforcement bars  as shown in drawings may be  necessary.    Substitution  of  different  size bars will be permitted only when authorized  by the engineer.

vi)	No part of the reinforcement, irrespective of  whether  the concrete  work is under construction or completed, shall be used for  conducting  electrical  currents.      Electrical Grounding  connections  shall  be  carefully  isolated from reinforcement.

vii)	The number and size of all steel bars, ties, stirrups  and other  members  of  the  reinforcement  shall  be  in exact accordance with the drawings and the  rods  shall  be  bent cold by the gradual and uniform application of force to the  shapes  and  dimensions  given  in the bar bending schedule supplied by the engineer.  These schedules shall conform to IS:1566.

viii)  	Bars  which  have  been   bent   wrongly   shall   not   be straightened, re bent and used without the permission of the  engineer.

ix) 	Reinforcement  shall  be  suitably  supported  by  steel or concrete spacers, care being taken  during  the  concreting  operation to  maintain  the  concrete cover specified.  All hooks links and stirrups shall be such  that  the  bars  when tied together  are  properly  braced.    If  possible,  the  reinforcement  shall  be  fabricated  with  frames  or mats before being fixed in the  forms.    Good  quality  ductile binding  wire  of  18 gauge shall be used to fix and secure  the reinforcement so that no  bars  will  be  disturbed  or displaced when  the  concrete  is  placed. Alternatively  welding  may  be  carried  out  to  secure  and   fix   the reinforcement instead of binding wire.  No concreting shall be  commenced  until  the bars have been properly fixed and  tied at their specified location and  have  been  inspected  and approved by the engineer.

9.3       WATER:

Water  for  all  work  shall  be fresh, clean and free from injurious  or  deleterious  materials  and  conforming   to IS:3025.  The contractor shall provide at his own cost for distribution,  storage,  filtration  and / or treatment, as  necessary of the required quality of  water.    Quality  of  water to be used in concrete shall be such as to obtain the  consistency specified.    This  quality  of  water shall be  subject to approval by the engineer on the  basis  of  test finding and shall in no case be changed without permission.  The  suitability  of  water  for  making  concrete shall be ascertained by the compressive strength and initial setting  time test specified in IS:456.

9.4     GAUGING WATER:

The general arrangements for the supply of water for mixing  concrete  shall  be to the satisfaction of the engineer who  will determine the quantity of water to be used to  the  mix  according  to the degree of moisture in the aggregate.  The quantity of water thus determined shall  be  accurately measured for each separate mixing in a suitable container.

9.5   WORK TEST SHALL BE PERFORMED ACCORDING TO THE FOLLOWING SCHEDULE:

Six (6) cubes of 15 cm sides for every 150 m³ of  concrete  or for a shift of eight hours of concreting, of which three (3)  shall  be  tested  at  seven (7) days and three (3) at  twenty eight (28)  days.    Concrete shall be considered unsatisfactory if the average strength of three - 28 days cubes is below the value.  However, only one of  the  three  consecutive  tests may give a value less than the specified  strength but this  shall  not  be  less  than  90%  of  the specified strength.

Samples shall be taken while concrete is being poured in the presence of representatives appointed by the engineer and the contractor.    Proper record of work test shall be maintained and signed jointly.  The preliminary test and works tests shall be at the contractor's expense.

Unless  otherwise  specified,  the contractor shall provide all sand, coarse aggregate, cement  and  concrete  required  for  testing  and  all  handling,  transport  and all other services entitled in supplying the samples to  the  testing laboratory .    The  cost  of  the  supply of materials and facilities shall be deemed to be  included  in  the  quoted  rates.

9.6       CONSISTENCY AND WORKABILITY OF THE CONCRETE:

9.6.1	Consistency and workability of concrete shall be checked by measuring  the  slump  of  a  truncated  cone  of  concrete  straight  from  the  mixer under normal working conditions. The conical mould shall be of metal, 300 mm high - 100 mm & 200 mm in diameter at the top and base respectively.

9.6.2  	Moulds shall be prepared by the contractor.

To maintain the consistency of concrete, slump test as per IS-1199 shall be carried out at contractor’s cost every two hours during work progress or at intervals established by the Engineer, in addition to the slump test to be carried out while making cubes. The table below gives the general slump range to be followed for various  types  of  construction  unless otherwise shown in drawings or instructed by the engineer.

Various types of construction               	 		Slump mm

Max.  			 Min.

Reinforced walls and footings            		 80     			30

Plain footings, caissons and            		 75     			25

substructure walls

Slabs, beams and reinforced walls        		100     			25

Various types of construction               	 		Slump mm

Max.  			 Min.

Pumps and other misc. equipment foundations 75  			25

Building columns                          			100    			25

Pavements                                  		 	50     			25

Heavy mass construction                    		   50     		   25

The workability test by means of compaction factor tests as  per IS:1199 shall also be carried out by the contractor  at   his cost.

9.7   	OPTIONAL TESTS:

[

The  engineer,  if  he  so  desires,  may order tests to be  carried out on cement, sand,  coarse  aggregate,  water  in  accordance  with  the  relevant  Indian Standards.

Tests on cement shall include

(i)	Fineness test

(ii) 	Test for normal consistency

(iii) 	Test for  setting  time

(iv) 	Test for soundness

(v)	Test for tensile strength

(vi) 	Test for compressive strength

(vii)	Test for heat of hydration (by experiment and by calculations) in accordance with IS:269.

Tests on sand shall include

(i) 	Sieve test

(ii) 	Test for organic impurities

(iii) 	Decantation test  for  determining  clay  and  silt content

(iv) 	Specific gravity test

(v) 	Test for unit weight and bulkage factor

(vi) 	Test for sieve analysis and fineness modulus

Tests on coarse aggregate shall include

(i)	Sieve analysis

(ii)  	Specific gravity and  unit weight of dry, loose and rodded aggregate

(iii) 	Soundness and alkali aggregate reactivity

(iv) 	Petrographic examination

(v) 	Deleterious materials and organic impurities

(vi)	Test for aggregate crushing value.

Any or all these tests would  normally  be  ordered  to  be  carried  out  only  if the engineer feels the materials are not in accordance to the specification or if the  specified  concrete  strengths  are not obtained and shall be performed by the contractor at an approved testing laboratory  at  his  cost.

If  the work cubes do not give the stipulated strengths the engineer reserves the right to ask contractor to  dismantle  such  portions  of  the  work  which  in  his  opinion  are  unacceptable and redo the work to  standard  stipulated  at  contractor's cost.    The contract price for concrete shall be all inclusive, including making preliminary  mix design and test cubes, works  cubes,  testing  them  as  per specification, slump tests, optional tests etc., complete.

9.8       STORAGE:

a)	GENERAL: All materials shall be so stored as to prevent deterioration or intrusion of foreign matter and to ensure the preservation of their quality and fitness for the work. Any material, which has deteriorated or has been damaged or is otherwise considered defective by the Engineer, shall not be used for concrete and shall be removed from site immediately, failing which, the Engineer shall be at liberty to get the materials removed and the cost incurred thereof shall be realized from the contractor's dues. The Contractor shall maintain up to date accounts of receipt, issue and balance (stack wise) of all materials. Storage of materials shall conform to IS: 4082. General storage shall be carried out by the contractor in a manner affording convenient access for identification and inspection at all time. The storage facilities shall be subject to approval of the Engineer-in-charge.

b) 	CEMENT: Sufficient space for storage, with open passages between stacks, shall be arranged by the Contractor to the satisfaction of the Engineer. Cement shall be stored off the Ground in dry, weather proof, leak proof, well ventilated ware-houses at the works in such a manner as to prevent deterioration due to moisture or intrusion of foreign matter. Cement shall be stored in easily countable stacks with consignment identification marks. Consignments shall be used in the order of their receipts at site. Sub-standard or partly set cement shall not be used and shall be removed from the site, with the knowledge of the Engineer, as soon as it is detected. Cement hold in storage for a period of 90 days or longer shall be tested at an approved laboratory before being put to use.

c) 	AGGREGATES : Aggregates shall be stored by the contractor in areas floored with tightly laid wooden planks or other approved hard, smooth and clean surface, in a manner precluding intrusion or foreign material. Each size shall be kept separated with wooden or steel or concrete or masonry bulk-heads or in separate stacks and sufficient care shall be taken to prevent the material at the edges of the stockpiles from getting intermixed. Stacks of fine and coarse aggregates shall be kept sufficiently apart with proper arrangement of drainage. The aggregates shall be stored in easily measurable stacks of suitable depths as may be directed by the Engineer.

- REINFORCEMENT: Reinforcing steel shall be stored consignment wise and size wise off the Ground and under cover, in a manner to prevent object ionic changes in original surface characteristics. It shall be protected from rusting, oil, grease and distortions. If necessary, the reinforcing steel may be coated with cement wash before stacking to prevent scale and rust at no extra cost to the purchaser. The stacks shall be easily measurable. Steel needed for immediate use shall only be removed from storage. Reinforcement shall be stored in separate piles or racks above grade.

9.9      QUALITY CONTROL:

Contractor shall establish and maintain quality control for different items of work and materials as may be directed by the Engineer to assure compliance with contract requirements and maintain and submit to the Engineer records of the same. The quality control operation shall include but not be limited to the following items of work:

a) 	Admixture: Type, quantity, physical and chemical properties that affect strength, workability and durability of concrete. For air entraining admixtures, dosage to be adjusted to maintain air contents within desirable limits.

b) 	Aggregate: Physical, chemical and mineralogical qualities. Grading, moisture content and impurities.

c) 	Water: Impurities tests.

d) 	Cement: Tests to satisfy relevant IS Specifications (only association with purchaser's tests, if the supply is made by purchaser).

e) 	Formwork:  Material, shapes, dimensions, lines, elevations, surface finish, adequacy of form, ties, bracing & shoring and coating.

f)	 Reinforcement: Shapes, dimensions, and length of splices, clearances, ties and supports. Quality and requirement of welded splices. Material tests or certificates to satisfy relevant IS Specification (if contractor's supply).

g) 	Grades of concrete: Usage and mix design, testing of all properties.

h) 	Batching & Mixing: Types and capacity of plant, concrete mixers and  transportation  Equipment.

i) 	Joints: 	Locations of joints, water stops and filler materials. Dimension of joints, quality and shape of joint material and splices.

j)	Embedded and Anchorage items: Material, shape, location, and setting.

k) 	Placing: Preparation, rate of pouring, weather limitations, time intervals between mixing and placing and between two successive lifts, covering over dry or wet surfaces, cleaning and preparation of surfaces on which concrete is to be placed,

application of mortar/slurry for proper bond, prevention of cold joint, types of chutes or conveyors.

l)	Compaction: 	Number of vibrators, their prime mover, frequency and amplitude of vibration, diameter and weight of vibrators, duration of vibration, hand-spreading, rodding and tamping.

m) 	Setting of base and beaming plates: Lines, elevations and bedding mortar.

n) 	Concrete finishes: Repairs of surface defects, screening, floating, steel trowel ling and brooming, special finishes.

o) 	Curing: Methods and length of Copies of records and tests for the items noted above, as well as, records of corrective action taken shall be submitted to the Engineer for approval as may be desired.

9.10      INSTALLATION:

All installation requirements shall be in accordance with IS:456 and as supplemented or modified herein or by other best possible standards where the specific requirements mentioned in this section of the specification do not cover all the aspects to the full satisfaction of the Engineer.

9.11 	GRADES OF CONCRETE:

A)	Concrete shall be either ordinary or controlled and in grades designated M-10, M-15, and M-20 as specified in IS: 456 (latest edition). In addition, nominal mixes of 1:2:4; 1:3:6 and 1:4:8 of nominal size aggregate of 20 mm maximum or as indicated on drawings, by volume or any other mix as per requirement shall be used where specified.

B)	CONTROLLED CONCRETE:

  - General: Controlled concrete shall be used on all concrete works, except where specified.

  - Mix Proportions: The mix proportions for all grades of concrete shall be designed to obtain strength corresponding to the values specified in IS: 456 for respective grade of concrete. Preliminary tests, as specified in the IS code or as required by the Engineer-in-charge, shall be carried out sufficiently ahead of the actual commencement of the work with different grades of concrete made from representative sample of aggregates and cement expected to be used on the job to ascertain the water cement ratio required to produce a concrete having specified strength and sufficient workability to enable it to be well consolidated and to be worked into corners of shuttering and around the reinforcement.

C)	MIXES DESIGN CRITERIA: Concrete mixes will be designed by the Contractor to achieve the strength, durability and workability necessary for the job, by the most economical use of the various ingredients. In general, the design will keep in view the following considerations:-

a) 	Consistent with the various other requirements of the mix, the quantity of water should be kept at the lowest possible level.

b) 	The nominal maximum size of coarse aggregate shall be as large as possible within the limits specified.

  - The various fractions of coarse and fine aggregates should be mixed in such a proportion as to produce the best possible combined internal grading giving the densest and most workable mix.

d) 	The finished concrete should have adequate durability in all condition, to withstand satisfactorily the weather and other destruction agencies that it is expected to be subjected to in actual service. The requirement of adequate structural strength is catered for by the choice of proper grade of concrete by the Engineer. The Contractor will strictly abide by the same in his design of concrete mix installation .Not withstanding anything mentioned in various tables given in IS:456 giving specific values and degrees of workability for different condition of concrete placing, minimum cement content and maximum water cement ratio for concrete exposed to sulphate attack and for concrete to ensure durability under different condition of exposure, strength requirement for different grades of concrete, proportion for nominal mix concrete, the following tables in the specification are included. For identical condition if values given in the tables shown herein below are different from those mentioned in IS: 456, the values as indicated in the table shown herein below shall prevail.

TABLE - II

MINIMUM CEMENT CONTENT SPECIFIED FOR DIFFERENT GRADES OF CONCRETE

------------------------------------------------------------------------------------------------------

Grade of 		              Minimum Cement Content/m³

Concrete 		           Concrete of finished

---------------------------------------------------------------------------------------------------------

M –20 (design mix)             			330 kg

M – 25 (design mix) 				360 kg

-------------------------------------------------------------------------------------------------------

- The minimum cement contents mentioned in Table III are for average conditions. The Engineer-in-charge shall have the right to revise the minimum cement content.

In this connection the Contractor shall abide by the following conditions.

  - The contractor shall design the mixes for 10% (Ten per cent) higher strength over and above those specified in Table I under Clause 11.11(C), for the various grades of concrete and different slump requirements.

  - Sufficient number of trial mixes (to be decided by the Engineer) will be taken at the laboratory for the various designs and graphs of w/c ratio Vs crushing strengths at various ages will be plotted.

  - All tests will be done in presence of the Engineer who shall be the final authority to decide upon the adoption of any revised minimum cement content. The contractor will always be responsible to produce quality concrete of the required grade as per the acceptance criteria of IS:456.

  - The Engineer will always have the unquestionable right to revise the minimum cement content as decided above, if, in his opinion, there is any chance of deterioration of quality on account of use of lower cement content or any other reason.

At least four trial batches are to be made and 7 test cubes taken for each batch noting the slump of each mix. The cubes shall then be properly cured and two cubes for each mix shall be tested in a testing laboratory approved by the Engineer-in-Charge at 7 days and others at 28 days for obtaining the compressive strength. The test reports shall be submitted to the Engineer-in-Charge. The cost of the mix design and testing shall be borne by the Contractor. All tests shall be done in the presence of Engineer-in-Charge.

Concrete tests specimens shall be made, cured and tested in conformation with IS: 517 (latest edition). These tests shall be conducted at approved laboratory. The modules  and materials for cubes shall be supplied by the contractor who shall also arrange to transport the cubes/cylinders to laboratory at his cost.

The reports for each tentative concrete mix submitted for review shall include the following information.

i) 	Slump on which the design is based.

ii) 	Total liters of water per cubic meter.

iii) 	Water cement ratio.

iv) 	Ratio of fine to total aggregates.

v) 	Weight (surface dry) of each aggregate per cubic meter.

vi) 	Quantity of each admixture.

vii) 	Air content, if any.

viii) 	Compressive strength based on 7 days and 28 days compression tests.

ix) 	Time of initial set.

x) 	Time of final set.

xi) 	Weight of cement used in the mix.

- On the basis of the above reports, a proportion of mix by weight and water cement ratio shall be approved by the Engineer-in-Charge which will be expected to give the required strength, consistency and workability and the proportions so decided for different grades of concrete shall be adhered to during all concreting operations. If however, at any time, the Engineer-in-Charge feels that the quality of material being used has changed from those used for preliminary mix design, the Contractor shall have to run similar trial mixes to ascertain the mix proportions and water cement ratio for obtaining the desired strength and consistency. The design mix particulars shall indicate by means of graphs and curves etc. the extent of variation in the grading of aggregate, which can be allowed.

- In designing the mix proportions of concrete, the quantity of both cement and aggregate shall be determined by weight. The Engineer-in-charge may allow the quantity of aggregates to be determined by equivalent volume basis after the relationship between the weight and volume is well established by trial and the same shall be verified frequently. Water shall be either measured by volume in calibrated tanks of weighed. All measuring equipments shall be maintained in a clean and serviceable condition, and their accuracy periodically checked.

- To keep the water cement ratio to the designed value, allowance shall be made for the moisture contents in both fine and coarse aggregates and determination of the same shall be made as frequently as directed by the Engineer-in-Charge. The determination of moisture contents shall be according to IS: 2386 (Part-III).

- It will be within the competency of the Engineer-in-Charge to reduce the number of trial batches and the number of test specimens mentioned above. Further the Engineer-in-Charge can also allow adoption of the mixes already tried and found satisfactory, with similar materials, for other jobs at the same site without any fresh design of mix.

D)	    STRENGTH REQUIREMENTS:

i)	The mix proportions for all grades of concrete shall be designed to produce the grade of concrete having the required workability and a characteristic strength not less than the value given in Table-I vide Cl.11.11(C).

ii)	Should the work strength of concrete fall below the specified strength, the Engineer shall decide:

to reject the work, in which case the contractor shall replace the defective work with concrete of required strength and bear all costs for dismantling and replacing including the cost of associated form work, reinforcement, embedded parts and associated work.

(Or)

to accept the work at a reduced rate, in which case the unit rate payable for substandard work will be reduced by the owner directly in proportion to the work strength as compared to the specified strength.  The owner may, in addition, require other tests performed on the respective structural member so accepted prior to its acceptance with or without necessary/corrective measures and in each such case the contractor shall bear all costs for all such tests or corrective measures, besides the reduction in the unit rates as specified herein.

Concrete of strength below fifteen (15) percent of the specified strength will not be accepted.

iii)	With permission of the Engineer-in-charge, for any of the above mentioned grades of concrete, if the water quantity has to be increased in special cases, cement shall also be increased proportionately to keep the ratio of water to cement same as adopted in trial mix design for each grade of concrete. No extra payment for the additional cement will be made.

E)	DURABILITY REQUIREMENT:

Tables 19 & 20 of IS:456 give the maximum water-cement ratio permissible from the point of view of durability of concrete subjected to adverse exposure to weather, sulphate attacks, and contact with harmful chemicals. Impermeability may also be a important consideration.

Whenever the water-cement ratio dictated by durability consideration is lower than that required from strength criterion, the former shall be adopted. However, water cement ratio, from the point of view of durability as well as from strength consideration, should meet the requirements given in Table No.II.

TABLE-V

LIMITS OF CONSISTENCY

-------------------------------------------------------------------------------------------------------------

Degree of 		Slump in mm with Standard	   Use for which concrete is suitable

Workability                 Cone as per IS: 1199

Min.            Max	            -------------------------------------------------------------------------------------------------------------

Very low                      0                  25                  Large Mass concrete structure with heavy

compaction equipments, roads and like

Low                             25                 50                 Un-congested wide and shallow RCC

structures

Medium                       50                 100               Deep but wide RCC with congestion or

reinforcement and inserts

High                           100                150           	Very narrow and deep RCC structures with inserts congestion due to reinforcement and

-------------------------------------------------------------------------------------------------------------

(Note:  Notwithstanding anything mentioned above, the slump to be obtained for work in progress shall be as per direction of the Engineer).

The workability of concrete shall be checked at frequent intervals by slump tests. Alternatively where facilities exist or if required by the Engineer, the compacting factor test in accordance with IS:1199 and Clause 6 of IS:456 shall be carried out.

F) 	BATCHING:

i)	In proportioning concrete, the quantity of both cement and aggregate should be determined by weight, where the weight of cement is determined on the basis of weight of cement per bag, a responsible number of bags should be weighed periodically to check the net weight. Where the cement is weighed on the site and not in bags it should be weighed separately from the aggregates. Water should be either measured by volume in calibrated tanks or weighed. Any solid admixture that may be added, may be measured by weight, liquid and paste admixture by volume or weight. Batching plant where used should conform to IS:4925-1968. All measuring equipment should be maintained in a clean serviceable condition, and their accuracy periodically checked.

ii)	Except where it can be shown to the satisfaction of the Engineer-in-charge that supply on properly graded aggregate of uniform quality can be maintained over the period of work, the grading of aggregate should be controlled by obtaining the coarse aggregate in different sizes and blending them in the right proportion when required, different sizes being stocked in separate stock files. The grading of coarse and fine aggregate should be checked frequently for a given job being determined by the Engineer-in-charge to ensure that the specified grading is maintained.

iii)	Change from weigh batching to volume batching may be done only after obtaining the specific permission of Engineer-in-charge in writing.

iv)	The amount of the added water shall be adjusted to compensate for any observed variations in the moisture contents. For the determination of moisture content in the aggregates, IS:2386 (Part-III) may be referred to. To allow for the variation in their moisture content, suitable adjustments in the weights of aggregate shall be made. In the absence of exact data, only in the case of Nominal Mixes, the amount of surface water may be estimated from the values given in Table-C.

TABLE-C

SURFACE WATER CARRIED BY AGGREGATE

Aggregate                                                   Approximate Qty. of surface water

Percent by Mass                         Liter M

Very wet sand                                                   7.5                                             120

Moderately wet sand                                         5.0                                               80

Moist sand                                                         2.5                                               40

Moist gravel or crushed rock                        1.25-2.5                                        20-40

No substitutions in materials used on the work or alterations in the established proportions, except as permitted in Clauses 11.11(F)(iii) & (iv) shall be made without additional tests to show that the quality and strength of concrete are satisfactory.

9.12     WORKMANSHIP:

A)	GENERAL:

All workmanship shall be according to the latest and best possible standards. Before starting a pour the Contractor shall obtain the approval of the Engineer-in-Charge in a "Pour Card" maintained for this purpose. He shall obtain complete instructions about the material and proportion to be used, slump, workability, quantity of water per unit of cement, number of test cubes to be taken, type of finishing to be done, any admixture to be added, any limitation on size of pour and stopping of premature pours.

B)	MIXING OF CONCRETE:

All control/design mix concrete shall be mixed at a single central batching plant situated within the area allocation for the Contractor's particular use as shown on the drawings. The plant shall have mechanically operated mixer of an approved size and type capable of ensuring a uniform distribution of the materials throughout the mass. The entire batch shall be discharged before recharging.

The proportions of the fine and coarse aggregate, cement and water shall be as determined by the mix design or according to fixed proportions in case of nominal mix concrete and shall always be approved by the Engineer-in-Charge. The quantities of the cement, fine and coarse aggregates shall be determined by weight, the water shall be measured accurately after giving proper allowance for surface water present in the aggregate for which regular check shall be made by the Contractor.

The water shall not be added to the mix until all the cement and aggregates constituting the batch are already in the drum and dry mix for at least one minute. Mixing of each batch shall be continued until there is a uniform distribution of the materials and the mixing done for less than two (2) minutes and at least forty (40) revolutions after all the materials and water are in the drum. When absorbent aggregates are used or when the mix is very dry, the mixing time shall be extended as may be directed by the Engineer-in-Charge. Mixers shall not be loaded above their rated capacity as it prevents thorough mixing. If there is segregation after unloading form the mixer the concrete should be remixed.

Before beginning a run of concrete all partially set or hardened concrete and foreign material shall be removed from the inner surfaces of mixing and conveying equipment. The first batch of concrete, through a cleaned mixer, for use in the works, shall contain 10% additional cement at no extra cost to the owner, to allow for loss in the drum.

C)	CONVEYING CONCRETE:

a)	Concrete shall be handled and conveyed from the place of mixing to the place of laying as rapidly as practicable by approved means and placed and compacted in the final position before the initial setting of the cement starts. Concrete should be conveyed in such a way as will prevent segregation or loss of any of the ingredients. For long distance haulage, agitator cars of approved design will be used. If, in spite of all precautions, segregation does occur during transport, the concrete shall be properly remixed before placement. During very hot or cold weather, if directed by the Engineer, concrete shall be transported in deep containers which will reduce the rate of loss of water by evaporation or loss of heat. If necessary, the container may have to be covered and insulated. Conveying equipments for concrete shall be well maintained and thoroughly cleaned before commencement of concrete mixing. Such equipments shall be kept free from set concrete. Concrete shall not be delivered by spout or troughs nor dumped into carriers with a free fall from the mixer of more than 1 nut.

b)	No concrete shall be placed except in the presence of the Engineer-in-Charge or his authorized representative. Concrete which is not placed in accordance with the specifications or which is of inferior quality as determined by the Engineer-in Charge, shall be removed and replaced by the Contractor, the entire cost of which shall be borne by the contractor.

c)	Before any concrete is placed, the entire placing programme consisting of equipment, layout, proposed procedure and methods shall be submitted in writing to the Engineer-in-Charge for approval and no concrete shall be placed until his approval has been received.

d)	Concrete shall be conveyed to the point of final deposit by methods which will prevent the separation or loss of the ingredients. Concrete shall be deposited in its final position without moving it laterally in the forms for a distance in excess of 1.5 meters.

D)        Placing and Compacting Concrete:

a)	Where specifically covered, the relevant IS Code will be followed for the procedure of surface preparation, placement, consolidation, curing, finishes, repairs and maintenance of concrete. If, however, there is no specific provision in the relevant IS Code for any particular aspect of work, any other standard code of practice, as may be specified by the Engineer, will be adopted. Concrete may have to be placed against the following types of surfaces:

- Earth foundation

- Rock foundation

iii)	Formwork

iv)        Construction joint in concrete or masonry.

The surface on or against which concrete is to be placed has to be cleaned thoroughly. Rock or old construction joint has to be roughened by wire brushing, chipping, sand blasting or any other approved means for proper bond. All cuttings, dirt, oil, foreign and deleterious material, laitance, etc. are to be removed by air water jetting or water at high pressure. Earth foundation on which direct placement of concrete is allowed, will be rammed and consolidated as directed by the Engineer such that it does not crumble and get mixed up with the concrete during or after placement, before it has sufficiently set and hardened.

b)	Formwork, reinforcement, preparation of surface, embedment, joint seals etc., shall be approved in writing by the Engineer before concrete is placed. As far as possible, concrete shall be placed in the formwork by means approved by the Engineer and shall not be dropped from a height or handled in a manner which may cause segregation. Any drop over 1500 mm shall have to be approved by the Engineer.

c) 	Rock foundation or construction joint will be kept moist for at least 72 hours prior to placement. Concrete will be placed always against moist surface but never on pools of water. In case the foundation cannot be dewatered completely, special procedure and precaution, as directed by the Engineer will have to be adopted.

d)	Formwork will be cleaned thoroughly and smeared lightly with form oil or grease of approved quality just prior to placement. Before concrete is placed, forms, reinforcement, anchor bolts and embedment shall be rigidly secured in proper position. Concrete shall be deposited in its final position without segregation, rehandling or following or loss of liquid from concrete. The interval between adding the water to the dry materials in the mixer and the completion of the final placing inclusive of compaction of the concrete shall be well within the initial setting time for the particular cement in use or as directed by the Engineer-in-charge.

e) 	A layer of mortar of thickness 12 mm of the same or less w/c ratio and the same proportion as that of the concrete being placed and cement slurry will be spread thoroughly on the rock foundation or construction joint just prior to placement of concrete. The cost of application of such cement slurry and mortar will be deemed to be included in the unit rate of concrete.

f)	To ensure bond and water tightness between old concrete surface and the concrete to be placed, the surface should be cleaned and roughened by "initial green out" by wire brushing or chipping. The initial green cutting may be done after 6 hours of placing concrete in order to facilitate the work. Before plastering, the surface shall be thoroughly hacked. The bonding of old and new concrete should be done by applying the cement slur after thoroughly watering the old concrete surface and removing all free particles.

g)	The placing of concrete shall be a continuous operation with no interruption in excess of 30 minutes between the placing of continuous portions of concrete.

h) 	After concrete has been placed, it shall be spread, if necessary and thoroughly compacted by approved mechanical vibration to maximum subsidence without segregation and thoroughly worked around shape. To secure maximum density and eliminate formation of air pockets, the concrete shall be thoroughly vibrated and worked around all reinforcement, embedded facilities and into corners or forms during and immediately after placing. Unless other methods are authorised by the Engineer-in-charge, mechanical vibrators conforming to IS: 2505, IS: 2506, IS: 2514 and IS: 4656 (all latest edition) shall be used for this purpose, the  type and operation of which is subject to the approval of the Engineer-in-charge. The extent of vibration shall be through the entire depth and width of each new layer. Duration of vibration shall be sufficient to accomplish thorough compaction and complete embedment of reinforcement. Due to vibration , the tendency for large aggregate to gravitate to lower elevations shall not relieve the contractor from his responsibility of obtaining a uniform density throughout the mass. Excess cement paste thus formed at the top of each layer shall be removed before the succeeding layer is deposited.Vibrators shall not be used for pushing concrete into adjoining areas. Vibrators must be operated by experienced workmen and the work carried out as per relevant IS Code of Practice. In thin members with heavy congestion of reinforcement or other embedment, where effective use of internal vibrator is, in the opinion of the Engineer, doubtful, in addition to immersion vibrators the contractor may have to employ form vibrators conforming to IS:4656. For slabs and other similar structures, the contractor will additionally employ screed vibrator as per IS:2506. Hand tamping may be allowed in rare cases, subject to the approval of the Engineer. Care must be taken to ensure that the inserts, fixtures, reinforcement and formwork are not displaced or distorted during placing and consolidation of concrete. Contractor shall provide proper equipment or methods for compaction of concrete or covers or other similar areas where conventional methods would not be adequate.

i)	Immersion type vibration shall be provided at the rate of at least one 65 mm unit per cu.m. per hour together with at least one stand by vibrator of the appropriate size. Vibrators shall be inserted in the concrete at a sufficient number of places so that their fields of influence overlap and shall not be used to work the concrete along with forms or screeds. Vibrators shall be withdrawn causing segregation; surface laitance or leakage through the forms shall be avoided. Where electrically operated vibrators are used, diesel or petrol driven stand by vibrators shall be available for carrying on uninterrupted vibration in case of a power failure.

j)	Concrete  to be vibrated shall be placed in level layers of suitable thickness not greater than the effective length of the vibrator needle.  The concrete at the surface shall not  be distributed as horizontally as possible,  the  vibration  shall not  be  done  in  the  neighbourhood  of slopes.  The internal vibrator shall not be used to spread the  concrete for filling.    It is advisable to deposit concrete well in   advance of the point of vibration.  When  the  concrete  is being  continuously  deposited  to  a uniform depth along a member, vibrator shall not be operated too near to the free  end of the advancing  concrete,  usually  not within  1.20 meters of  it.    Every effort  shall  be made to keep the  surface of the previously placed layer of concrete alive so that the succeeding layer can be  amalgamated  with  it  by vibration process.   Following points shall be kept in mind while vibrating concrete.

k)	The  concrete  shall be placed in shallow layers consistent with the  method  being  used  to  place  and  vibrate  the  concrete.   Usually  concrete  shall be placed in thickness  not more than 300 mm and on initial  placing  in  thickness  not more than 150 mm.

l) 	The  vibrator head shall be dipped through filling which is  to be consolidated to further depth of 10 to 20 mm  in  the lowest layer which has already been consolidated.

m)	Vibration  shall  be  carefully  controlled,  the  internal  vibrator being systematically inserted  at  points  minimum 450  mm  and  maintained  in  position  for  a  fixed time.  Immersion for periods of 5 to 15 seconds should normally be  sufficient.  The limit  of  action  is  judged  by  surface appearance.   The surface shall neither be honey combed nor shall it contain excess mortar.

n) 	The vibrator shall be inserted vertically, with inclined or  haphazard insertion it will be impossible to  regulate  the degree of compaction in all portions of the concrete.  Care  shall  be  taken  to prevent contact of immersion vibrators with form work, reinforcement steel and finished  surfaces. Immersion   vibrators   shall  not  come  in  contact  with   reinforcement steel if initial set of  concrete  around  it   has started.

o)	The  vibrator  shall  be  allowed  to  penetrate on its own accord and should be withdrawn quite slowly, at the rate of about 75 mm per second, whilst  still  running,  so  as  to  allow the redistribution of the concrete in its wake.

p)	The rate of placement of concrete shall be such that no cold joint is formed and fresh concrete is placed always against green concrete that is still plastic and workable. No concrete shall be placed in open, is to be attempted unless sufficient tarpaulins or other similar protective arrangement for completely covering the still green concrete from rain is kept at the site of placement. If there has been any sign of washing of cement and sand, the entire affected concrete shall be removed immediately. Suitable precautions shall be taken in advance to guard against rains before leaving the fresh concrete unattended. No accumulation of water shall be permitted on or around freshly laid concrete.

q)	Slabs, beams and similar members shall be poured in one operation, unless otherwise instructed by the Engineer. In special circumstances with the approval of the Engineer-in charge, these can be poured in horizontal layers not exceeding fifty (50) cm. in depth. When poured in layers, it must be ensured that the under layer, is not already hardened. Bleeding of under layer if any, shall be effectively removed. Moulding, throating, drip course, etc. shall be poured as shown on the drawings or as directed by the Engineer. Holes shall be provided, and bolts,   sleeves, anchors, fastenings or other fixtures shall be embedded in concrete as shown on the drawings or as directed by the Engineer. Any deviation there from shall be set right by the Contractor at his own expense as instructed by the Engineer.

r)	Concrete shall be deposited in a manner to prevent displacing facilities or reinforcement above the level of the fresh concrete, and the formation of seams or planes of weakness within the sections. Each layer shall be deposited as close to its final position as practicable in order to prevent segregation.

s)	In case the forms or supports get displaced during or immediately after the placement and bring the concrete surface out of alignment beyond tolerance limits, the Engineer may direct to remove the portion and reconstruct or repair the same at the Contractor's expense.

t)	The Engineer shall decide upon the time interval between two placements of concrete of different ages coming in contact with each other, taking in consideration the degree of maturity of the older concrete, shrinkage, heat dissipation and the ability of the older concrete to withstand the load imposed upon it by the fresh placement.

u)	Once the concrete is deposited, consolidated and finished in its final position, it shall not be disturbed.

v)	Whenever vibration has to be applied externally the design of formwork and the disposition of vibrators shall receive special consideration to ensure efficient compaction and to avoid surface blemishes. After initial set of concrete the forms shall not be jarred and no strain or vibration equipment shall be placed on the ends of projecting reinforcement.

w)	Concrete shall not ordinarily be placed under water. In unavoidable cases, such concreting shall be done only with the specific approval of procedure and application by the Engineer-in-charge. The concrete shall contain at least 10 percent more cement than that required for the same mix placed in the dry, the quality of extra cement varying with condition of placing. The relevant clauses of IS:456 (latest edition) should be adhered to 11.12(D)(w). Re tamping of concrete or mortar which has partially hardened shall not be permitted.

x)	It is imperative that all excavations prepared for concrete construction be maintained free of water until such concrete work is completed. The contractor shall make provisions and furnish equipment as required for such dewatering, subject to approval by the Engineer-in-charge. Water used for flushing concrete placing equipment shall be discharged clear of the concrete and forms.

y)	Contractor shall keep an accurate record of the date on which the concrete is cast for each part of work and date on which the forms are removed.

E)        COLD WEATHER CONCRETING:

When conditions are such that the ambient temperature may be expected to be 4.5 °C or below during the placing and curing period, the work shall conform to the requirement of Clause 13 of IS:456 and IS:7861.

F)	HOT WEATHER CONCRETING:

When depositing concrete in very hot weather, the contractor shall take all precautions as per IS:7861 and stagger the work in the cooler parts of the day to ensure that the temperature of wet concrete used in massive structures does not exceed 38 °C while placing. Positive temperature control by pre-cooling, post cooling or any other method, if required, will be specified and paid for separately.

9.13    CONSTRUCTION JOINTS:

i)	The locations and details of construction joints must be got approved from the Engineer-in-charge before concrete is poured. Concreting shall be carried continuously up to construction joints.

ii)	At least two hours must lapse after depositing concrete in the columns or walls before depositing in beams, girders or slabs supported thereon. Beams, girders, brackets and haunches shall be considered as part of the floor system and shall be placed monolithically therewith.

iii)	Construction joints in foundations of equipment shall not be provided without specific concurrence of the Engineer-in-charge.

iv)	It is always desirable to complete any concrete structure by continuous pouring in one operation. However, due to practical limitation of methods and equipment and certain design considerations, construction joints are formed by discontinuing concrete at certain predetermined stages. These joints will be formed in a manner specified in the drawings/instruction. Vertical construction joints will be made with rigid stop board forms having slots for allowing passage of reinforcement rods and any other embedment and fixtures that may be shown of desired by the Engineer-in-charge keep and/or dowel bars shall be provided at the construction joints. For water retaining structures and leak proof buildings suitable and approved water stops may be installed at the construction joints as per Clause 12.4 of IS: 456. Where the location of the joints are not specified, it will be in accordance with the following:-

- In a column, the joint shall be formed 75 mm below the lowest soffit of the beam framing into it.

- Concrete in a beam shall preferably be placed without a joint, but if provision of a joint is unavoidable, the joint shall be inclined as given in the relevant standards.

- Joint in a suspended floor slab shall be vertical and between 1/4th to 1/3rd of the span from its ends and at right angles to the principal reinforcement.

- Feather-edges in concrete shall be avoided while forming a joint.

- A construction joint should preferably be placed in a low stress zone and at right angles to the direction of the principal stress.

- In case the contractor proposes to have a construction joint anywhere to facilitate his work, the proposal should be submitted well in advance to the Engineer for study and approval without which no construction joint will be allowed.

- When the work has to be resumed on a surface that has hardened, such surface shall be roughened. It shall then be swept clean, thoroughly wetted, and covered with a 15 mm layer of mortar composed of cement and sand in the ratio of 1:1.

This 15 mm layer of mortar shall be freshly mixed and placed immediately before the placing of the concrete. The new concrete shall be worked against the prepared surface before the slurry sets. Special care shall be taken to see that the first layer of concrete placed after a construction joint is thoroughly rammed against the existing layer. Old joints during pour shall be treated with 1:1 freshly made cement sand slurry only after removing all loose materials.

vi)	Where the concrete has not fully hardened, all laitance shall be removed by scrubbing the wet surface with wire or bristle brushes, care being taken to avoid dislodgement of particles of aggregate. The surface shall be thoroughly wetted and all free water removed. The surface shall then be coated with neat cement grout. The first layer of concrete to be placed on this surface shall not exceed 150 mm in thickness and shall be well rammed against old work, particular attention paid to concrete and close spots.

9.14  	REPAIRS & FINISHES OF CONCRETE:

A)	 Adequate and sound concrete surfaces, whether formed or unformed, can be obtained by employing a concrete mix of proper design, competent formwork, appropriate methods of handling, placing and consolidation by experienced workmen.

B)	All concrete surface either cast-in-site or pre-cast shall have even, clean finish, free from honey combs, air bubbles, fins or other blemishes.

C)	Unsound concrete resulting from improper mix design, incompetent methods, equipment and formwork, poor workmanship and protection will not be accepted and will have to be dismantled, removed and replaced by sound concrete at the Contractor's cost. The Engineer may, at his sole discretion, allow retaining concrete with minor defects provided the Contractor is able to repair it by approved methods at no extra cost to the Purchaser. All concrete work shall be inspected by the Contractor immediately after the forms are removed and he will promptly report occurrence of any defects to the Engineer. All repair works will be carried out as per the instructions and in the presence of the Engineer or his representative. Generally, repair work will consist of any or all of the following operations:-

- Sack rubbing with mortar and stoning with carborundum stone.

- Cutting away the defective concrete to the required depth and shape.

- Cleaning of reinforcement and embedment.

- Roughening by sand blasting or chipping.

- Installing additional reinforcement/welded mesh fabric.

- Dry packing with stiff mortar.

- Plastering, grunting, shotereting etc.

- Placing and compacting concrete in the void left by cutting out defective concrete.

- Grouting with cement sand slurry of 1:1 mix.

D)	The requirement of finishes of formed surfaces are given separately under Clause 13.6 of this specification. The Contractor is to include in his quoted rate for concrete, the provision of normal finishes in unformed surfaces which can be achieved by screening, floating, toweling etc., as and where required by the Engineer without any extra cost to the Purchaser. A few typical and common cases of treatment of concrete surface are cited below.

a)	Except where a special finish is called form all exposed concrete   shall be finished as follows.

b)	All fins and other projections shall be neatly chipped, rubbed down and made smooth; form oil shall be entirely removed by stiff fiber brushes. The use of acid shall not be permitted. All exposed corners shall be slightly rounded or chamfered.

Air holes, cavities and similar imperfections shall be first saturated with water and filled with a mortar mixture of composition as that used in the concrete. After initial set of mortar the surface shall be rubbed down with burlap. A stucco coat shall be allowed to be applied to the surface.

c)         i) Floor:

Whenever a non integral floor finish is indicated, the surface of reinforcement concrete slab shall be struck off at the specified levels and slopes and shall be finished with a wooden float fairly smooth removing all laitance. No over -toweling, to obtain a very smooth surface, shall be done, as it will prevent adequate bond with the subsequent finish. If desired by the Engineer, the surface shall be scored and marked without any extra cost to the Purchaser to provide better bond. Where monolithic finish is specified or required, concrete shall be compacted and struck off at the specified levels and slopes with a screed, preferably a vibrating type and then floated with a wooden float. Steel trowel ling is then started after the moisture film and shine have disappeared from the surface and after the concrete has hardened enough to prevent excess of fines and water to rise to the surface but not hard enough to prevent proper finishing of aberrations. Steel trowel ling properly done will flatten and smoothen sandy surface left by wooden floats and produce a dense surface free from blemishes ripples and trowel marks. A fine textured surface that is not slick and can be used where there is likelihood of spillage of oil or water can be obtained by trowel ling the surface lightly with a circular motion after initial trowel ling keeping the steel trowel flat on the surface. To provide a better grip the Engineer may instruct marking the floor in a regular geometric pattern after initial trowel ling.

ii) Beams, columns & walls:

If on such or any other concrete structure it is intended to apply plaster or such concrete surfaces against which brickwork or other allied works are to be built, the contractor shall hack the surface adequately as soon as the form is stripped off so that proper bond can develop. Pattern, adequacy and details of such hacking shall meet with the approval of the Engineer, who shall be informed to inspect such surfaces before they are covered up.

d)	Concrete surfaces to be subsequently plastered or where brickwork shall be built against it shall be adequately hacked as soon as the form is stripped off so that proper bond can develop.

9.15  CURING OF CONCRETE:

A)	Curing shall be as per this specification and IS: 456. Unless otherwise specified all concrete shall be moist cured by keeping all exposed surfaces, edges and corners continuously moist for at least twenty one days after being placed, by spraying, ponding or covering with waterproof paper or moisture retaining fabric.

B)	 Newly placed concrete shall be protected by approved means from rain, sun and wind. Concrete placed below the Ground level shall be protected against contamination from falling earth during and after placing. Concrete placed in Ground containing deleterious substances, shall be protected from contact with such Ground, or with water draining from such Ground, during placing of concrete and for a period of at least three days or as otherwise instructed by the Engineer. The Ground water around newly poured concrete shall be kept to an approved level by pumping out or other adequate means of drainage to prevent floatation or flooding. Steps, as approved by the Engineer, shall be taken to protect immature concrete from damage by debris, excessive loadings, vibration, abrasion, mixing with earth or other deleterious materials, etc. that may impair the strength and durability of the concrete.

As soon as the concrete has hardened sufficiently, it shall be covered either with sand, Hessian, canvas burlap or similar materials which will hold moisture for long period and prevent loss of moisture from concrete and kept continuously wet for at least 18 (eighteen) days after final setting. Curing by continuous sprinkling of water will be allowed if the Engineer is satisfied with the adequacy of the arrangements made by the Contractor.

Curing of concrete shall start after 8 hours of placement and in hot weather within 4 hours of placement of exposed faces. During the first 24 hours, the concrete shall be cured by use of wet burlap or such other means to cover the concrete surfaces. In very hot weather, precaution shall be taken to see that the temperature of wet concrete does not exceed 38 deg. C while placing.

Concrete slabs and floors shall be cured by flooding with water of minimum 25 mm depth for the period mentioned above. Approved curing compounds may be used in lieu of moist curing with the permission of the Engineer-in-charge. Such compounds shall be applied to all exposed surfaces of the concrete as soon as possible after the concrete has set.

The contractor shall remain extremely vigilant and employ proper equipment and workers under able supervision for curing. The Engineer's decision regarding the adequacy of curing is final. In case any lapse on the part of the contractor is noticed by the Engineer, he will inform the contractor or his supervisor verbally or in writing to correct the deficiency in curing. If no satisfactory action is taken by the contractor within 3 (three) hours of issuance of such instruction, the Engineer will be at liberty either to employ sufficient means through any agency to make good the deficiency and recover the cost thereof from the contractor, or pay for the part where adequate curing was noticed at a reduced rate, entirely at the discretion of the Engineer.

C)      WASH WATER:

Wash water shall be removed in a manner to prevent running down and staining of concrete surfaces which will be exposed at the completion of the work. Should unsightly wash water streak develop on the exposed surfaces, they shall be removed and water has to be lead to a suitable place as directed by Engineer- in charge.

9.16    METHOD OF MEASUREMENT:

A)	 Actual volume of work as executed as per drawing issued, whichever is less, shall be measured in cubic meter correct up to second place of decimal. Deductions for openings, conduits, pipes, ducts, pockets, chases etc. shall be made, provided they are larger than 0.1 m² in area (for each opening unto and less than 0.1 m² in area the formwork shall not be paid for separately).

B)	No deduction shall be made for embedded fixtures including reinforcements, sleeves, anchor bolts and similar items.

.

9.17    SAMPLING & TESTING IN FIELD:

A)       Grading Test:

Grading tests on coarse and fine aggregates shall be carried out at intervals specified  by the Engineer-in- charge.

B)      Slump Test or Concrete:

At least one slump test shall be made for every compressive strength test carried out.  More frequent test shall be made if there is a distinct change in work conditions, or if required by the Engineer -in charge

C)	 Strength test of concrete:

a)	 Samples of concrete shall be taken at the direction of the Engineer-in-charge in the field in accordance with IS: 1199 "Methodist of sampling and analysis of concrete".

b)	These shall be tested for strength and consistency at an approved Government laboratory as specified by the Engineer-in-charge in accordance with IS:517. The moulds and material for cubes and cylinders shall be supplied by the contractor who shall also arrange to transport the cubes/cylinders to laboratory at his cost. Actual cost of the testing shall be borne by the contractor.

c)	The acceptance criteria for the compressive strength shall be as per IS: 456. Only the slump indicated for the approved design mix shall be adopted. However, larger slumps than those indicated in approved design mix, of concrete of a specified grade (strength) may be necessary to get a workable consistency for concrete in case of beams, columns and other heavily reinforced members. No extra payment shall be made for extra cement that may have to be added in such cases to get the concrete of the same specified grade (strength) with larger slumps. The decision of Engineer-in-charge regarding the degree of consistency of the amount of slump shall be final.

d)	Samples shall be cured under laboratory conditions, except when in the opinion of the Engineer-in-charge extreme weather condition may prevail at which time the Engineer-in-charge may require curing under job conditions.

e)	If the test strength of the laboratory controlled cubes/cylinders for any portion of the concrete work falls below the compressive strength specified, the Engineer-in-charge shall have the right to order a change in the proportion or the water content for the remaining portion of the structure.

f)	If the test strength of the job cured cubes/cylinders falls below the specified strength, the Engineer-in-charge shall have the right to require provision for temperature and moisture control during curing as necessary to secure the required strength and may require retests in accordance with "Standard method of securing, preparing and testing specimens from hardened concrete for compressive and flexural strength or order load tests to be made on the portion of the building so affected. All such tests shall be made  contractor's expenses.

g)	When the cubes tested reveal a strength lower than those specified, the acceptance criteria for such concrete shall be decided as stipulated in IS:456 (latest edition). The Engineer-in-charge shall also reserve the right to reject whole or any part of the work. In case of acceptance of such works the standard deviations shall be worked out and examined by the Engineer-in-charge and if he is satisfied, only then such work can be accepted at the reduced rate. The amount to be deducted shall be decided by the Engineer-in-charge.

h)	For the purposes of statistical analysis any cube result, which in the opinion of Engineer-in-charge is due to improper sampling, molding or testing shall be discarded and a dummy result shall be substituted. The value of the cubes from the same grade of concrete tested immediately before and after the discarded value.

i)	The contractor shall prepare and submit to the Engineer-in charge a sample form to be used during the batching and mixing of the concrete. The form shall provide for entries to be made which will indicate the quantity of each material placed in each mixer, the mixer identification number, the batch number, the duration of time the batch was mixed, and the name or initials of the person recording the information.

j)	The contractor is responsible for recording the required information for each batch of concrete and for submitting the required number of copies of completed form to the Engineer-in charge.

k)	Strict quality control shall be exercised in all concreting works and the acceptance criteria of concrete shall be in accordance with IS: 456-2000.However, in exceptional circumstances the Engineer-in-charge may, at his discretion, accept a concrete of lower strength than specified and which is otherwise acceptable according to IS: 456-2000.

l)	Failure of the concrete to meet the early age strengths at 7 days shall be considered a failure of the concrete to meet the strength requirements and the Engineer-in-charge in such instances shall have the right to stop construction. The early age strength shall be the mean strength at the specified age minus 2 times standard deviation for the specified age as given in clause 11.21 (B) .

m)	Concrete work found unsuitable for acceptance shall be dismantled and replacement is to be done as per specification by the contractor. No payment for the dismantled concrete, the relevant form work and reinforcement embedded fixtures, etc. wasted in the dismantled portion shall be made. In the course of dismantled, if any damage is done to the embedded items or adjacent structures, the same shall be made good, free of charge by the contractor to the satisfaction of the Engineer-in-charge.

n)	The dimension of concrete as cast when compared with those on the drawings shall be within the tolerances specified on IS Code. No reduction will be permitted in the cover to reinforcement because of a specified negative tolerance in a concrete section.

o)	Only the slump indicated in the approved design mix shall be adopted. However larger slumps than those specified grade (strength) may be necessary to get a workable constituency for concrete in case of beams, columns and other heavily reinforced members. No extra payment shall be made for extra cement that may have to be added in such cases to get the concrete of the same specified grade (strength) with larger slumps. The decision of Engineer-in-charge regarding the degree of constancy or the amount of slump shall be final.

9.18          FREQUENCY OF SAMPLING:

The minimum frequency of sampling of concrete for each grade shall be in accordance the following:

Quantity of concrete                                       Number of samples

in the WORK M3

1 - 5 				                     1

6 –15					         2

17- 30					         3			              	 31-50 					         4

51 and above                         	4 Plus one additional     sample for each additional 50 M3 or part thereof.

A)	 Test Specimens: Six test specimens shall be made from each sample first testing three    at 7 days & after three at 28 days.

B)	Test Strength of Sample: The test strength of the sample shall be the average of the strength of three specimens. The individual variation should not be more than + 15 per cent of the average.

9.19	STANDARD DEVIATION:

A)        STANDARD DEVIATION BASED ON TEST RESULTS:

- Number of test results: The total of test results required to constitute and acceptable record for calculating of standard deviation shall be not less than 30. Attempts should be made to obtain the 30 test results, as early as possible, when a mix is used for the first time.

- Standard deviation to be brought up to date: The calculation of the standard deviation shall be brought up to date after every change of mix design and at least once a month.

- Concrete of each grade shall be analyzed separately to determine its standard deviations.

B)	Assumed Standard Deviation: Where sufficient test results for a particular grade of concrete are not available, the value of standard deviation given in Table D may be assumed.

T A B L E - D

ASSUMED STANDARD DEVIATION

Grade of concrete 			  	Assumed Standard Deviation		 							N/mm2

M-10 						     2.3

M-15 					                 3.5

M-20 						     4.6

However, when adequate past records for a similar grade exist and justify to the designer a value of standard deviation different from that shown in Table-D, it shall be permissible to use that value.

C)        IS Codes:

Important relevant IS for this Section:

IS: 456 	Code of practice for plain and reinforced concrete.

IS: 1199 	Methods of sampling and analysis of concrete.

IS: 1838 	Preformed fillers for expansion joints in concrete  non extruding and resilient type (bitumen impregnated filler).

IS: 2386 	Part III: Specific gravity, density, voids, absorption and buckling.

IS: 2505 	General requirements for concrete vibrators, immersion type.

IS: 2506 	Screed board concrete vibrators.

IS: 2514 	Concrete vibrating tables.

IS: 3025 	Methods of sampling and test (physical and chemical) for water used in industry.

IS: 3370 	Code of practice for concrete structure for the storage of liquids.

IS: 3350 	Methods of tests for routine control for water used in industry.

IS: 4656 	Form vibrators for concrete.

IS: 517 	Methods of test for strength of concrete.

10.0   TECHNICAL SPECIFICATION FOR REINFORCEMENT:

A)       SCOPE:

This section of the specification shall cover furnishing of working drawings with bar bending schedule and the furnishing, cleaning, bending placing with arrangements for chairs, supports and suitable covers if reinforcement steel plain or deformed for all reinforced concrete works, below and above Ground level for complete pits as per drawings and specification.

B)	Contractor shall supply, fabricate and place reinforcement to shapes and dimensions, as per IS:2502 "Code of Practice for bending and fixing bars for concrete reinforcement" and as indicated in approved drawings of the contractor.

C)      MATERIALS:

Mild steel round bars, cold twisted and deformed bars as medium tensile or high yield strength steel confirming to IS:432 and IS:1786-1979, plain hard drawn steel wire fabric etc will be used as reinforcement as per drawings and directions. Reinforcement accessories shall also be supplied by the contractor in the rates quoted for reinforcement.

D)     BAR BENDING SCHEDULES:

The contractor shall submit to the Engineer for approval Bar Bending Schedules with working drawings in triplicate, showing clearly the arrangements proposed by the contractor, within one month of receipt of the Letter of Intent or of the receipt of the relevant approved design of the drawings, whichever is later. Upon receipt of the Engineer's final approval of the Bar Bending Schedule and drawings, the contractor shall submit 6 (six) prints of the final drawings with one reproducible print after incorporating necessary modifications or corrections, for final record and distribution. Approval of such detailed drawings by the Engineer shall not relieve the contractor of his responsibility for correctness nor of any of his obligations to meet the other requirements of the contract. Any adjustments in reinforcement to suit field conditions and construction joints other than shown on approved drawings shall be subject to approval of Engineer-in-charge/consultant. The payment for above is deemed to have been included in the rates quoted for reinforcement item. The contractor shall adhere strictly to requirements for a concrete cover over steel reinforcement, projection of bars for bending with future extensions, reinforcement, mesh reinforcement and other items to connection with proper placing.

E)        CLEANING:

All steel for reinforcement shall be free from loose scales, oil, grease, paint or other harmful matters immediately before placing the concrete.

F)        BENDING:

a)	Unless otherwise specified, reinforcing steel shall be bent in accordance with the procedure specified in IS: 2502 or as approved by the Engineer. Bends and shapes shall comply strictly with the dimensions corresponding to the approved Bar Bending Schedules. Bar Bending Schedules shall be rechecked by the contractor before any bending is done and he shall be entirely responsible for its correctness. Bars correctly bent shall only be used.

b)	No reinforcement shall be bent when already in position in the work, without approval of the Engineer, whether or not it is partially embedded in concrete. Bars shall not be straightened in a manner that will injure the material. Re-bending bars shall be bent by machine or other approved means producing a gradual and even motion. All the bars shall be cold bent unless otherwise approved. Bending hot at a cherry red heat (not exceeding 845 deg. C) may be allowed under very exceptional circumstances except for bars whose strength depends on cold working. Bars bent hot shall not be cooled by quenching. Bars shall be properly lagged for easy identification.

c)	In no case shall the clear distance between bars be less than the diameter of the bar not less than one third of the max. size of coarse aggregate. Reinforcement shall be bent in accordance with procedure specified in IS:2502 code of practice for bending and fixing of bars for concrete reinforcement and shall not be straightened in manner that will injure the material.

d)	Expanded portion of reinforcement bars must not be subjected to impact or rough handling and workers will not be permitted to climb on bar extensions until the concrete has sufficient strength so that no movement of the bar in the concrete is possible.

e)	Where reinforcement bars are bent at site at construction joints and afterwards bent back into their original positions. Care should be taken to ensure that at no time is the radius of the bend less than 4x bar diameters for plain mild steel or 6 x bar diameters for deformed bars. Care shall also be taken when bending back bars, to ensure that the concrete around the bar is not damaged.

G)	SPLICING:

a)	All reinforcement shall be furnished in the full length indicated on the drawing. Splicing of the bars except where shown on the drawings will not be permitted without the written permission of the Engineer-in-charge.

b)	At a compression splice each pair of lapped bars may be in contact but the minimum clear spacing between the splice and the adjacent splice shall be that specified for adjacent single bars.

H)	PLACING IN POSITION:

a)	All reinforcements shall be accurately fixed and maintained in position as shown on the drawings by such approved and adequate means like mild steel chairs and/or concrete spacer blocks irrespective of whether such supports are payable or not. Bars intended to be contact at crossing points, shall be securely tied together at all such points by No.20 G annealed soft iron wire or by tack welding in case of Bar larger than 25 mm dia., as may be directed by the Engineer. Binders shall tightly embrace the bars with which they are intended to be in contact and shall be securely held. The vertical distance between successive layers of bars shall be maintained by provision of mild steel spacer bars. They should be spaced such that the main bars do not sag perceptibly between adjacent spacers. Before actual placing, the contractor shall study the drawings thoroughly and inform the Engineer in case he feels that placement of certain bars is not possible due to congestion. In such cases he should not start placing any bar before obtaining clearance from the Engineer.

b)	The reinforcement accessories shall be furnished by the contractor. The wire shall be of annealed iron wire quality. Bar supports, charis, spreaders, spacers and bolsters shall be sufficiently heavy to support the reinforcement steel properly and shall be approved by the Engineer-in-charge. No separate payment shall be made on account of the above and the unit rate shall be inclusive of the cost of binding wire, bar supports, chairs bolsters, spacers etc. However when steel is supplied by the owner/purchaser a detailed record of the above shall be kept for purpose of only calculating the theoretical consumption but not for payment.

I)         WELDING:

a)	Normal bond laps in reinforcement may be placed by lap or butt-welding reinforcement bars, if asked by the Engineer, under certain conditions. The work should be done with suitable safeguards in accordance with relevant Indian Standards & IS:2751 for welding of mild steel bars used in reinforced concrete construction as per IS: 2751 and IS:456. Welded mesh fabrics conforming to IS: 1566 may also be used if specified in the Schedule of items and drawings.

b)	Field welding of reinforcing bars will not be permitted without the written consent of the Engineer-in-charge. Where welding is permitted it must be at suitable staggered locations. Tests shall be made to prove that joints are of the full strength of bards connected. Welding of reinforcement shall be done in accordance with the recommendation of IS:2751. This clause applies to main and distribution steel only.

c)	In those places where welded reinforcement chairs, spacer trusses etc. are necessary like in deep raft etc. and have been detailed in the drawing, any welding necessary for fabrication of such trusses chair etc. is deemed to have been covered under the rates for reinforcement and such spacer, chairs, trusses etc. shall be measured and paid under the relevant reinforcement item. If any steel plates are used as gussets in fabrication of these chairs, trusses the same shall be payable under insert item.

J)         CONTROL:

a)	The placing of reinforcements shall be completed well in advance of concrete pouring. Immediately before pouring, the reinforcement shall be examined by the Engineer for accuracy of placement and cleanliness. Necessary corrections as directed by him shall be carried out. Laps and anchorage lengths of reinforcing bars shall be in accordance with IS:456, unless otherwise specified. If the bars in a lap are not of the same diameter, the smaller will guide the lap length. The laps shall be staggered as far as practicable and as directed by the Engineer and not more than 50% of the bars shall be lapped at a particular section. Arrangements for placing concrete shall be such that reinforcement in position does not have to bear extra load and get disturbed.

b)	Covers for Reinforcement:

The cover for concrete over the reinforcements shall be as shown on the approved drawings unless otherwise directed by the Engineer. Care should be taken to ensure that projecting ends of ties and other embedded metal do not encroach into the concrete cover. Where concrete blocks are used for ensuring the cover and positioning reinforcement, they shall be made of mortar not leaner than 1 (one) part cement to 2 (two) parts sand by volume and cured in a pond for at least 14 (fourteen) days. The type, shape, size and location of the concrete blocks shall be as approved by the Engineer. Their strength shall correspond to the strength of concrete proposed for the structure. Where such cover blocks are used, all cover, spacers shall be secured firmly so that they are not disturbed during vibration.

c) 	Tolerances:

Unless otherwise specified by the Engineer-in-charge, reinforcement shall be placed within the following tolerances as specified in Clause 11.3 of IS: 456-2000:

    - For effective depth 200 mm or less + 10 mm

(b)       For effective depth more that 200 mm + 15 mm

The cover shall in no case be reduced by more than one third of specified cover or 5 mm whichever is less.

K)        STORAGE:

----------------------------------------------------------------------------------------------------

Storage 		Place of storing			 Remarks

---------------------------------------------------------------------------------------------------

A. Cement 		to be stored in a place of 		Test of compression

easy access for	 proper inspection	strength should be

and identification.  It should be	done by the project

placed in a weather-proof building,	authorities and result

so that loss due to dampness		should be intimated to

and other causes and is minimum.	the contractor from time

to time.

B. Reinforcement	Reinforcement procured by the          Steel shall not contain

bidder are to be stored diameter-	excess rust or cracks

wise in such a place to permit		etc.

easy identification. The area should

be such that water does not accumulate

and reinforcement do not get distorted.

It should not be stacked directly

over Ground or near any harmful

materials. It should be cleaned of

excessive rust before use.

--------------------------------------------------------------------------------

L)	ACCEPTANCE CRITERIA:

Reinforcements shall be checked for cleanliness, proper bending, binding,  placing and securing in position with provision for proper cover.

M)     METHOD OF MEASUREMENTS:

a)	Bar or any other type of reinforcement used like hard drawn steel wire fabric etc. for reinforced concrete shall be measured by weight in tonnes. The weight shall be arrived at by multiplying the actual or theoretical length measured along standard hooks, cranks, bends, authorized laps etc. whichever is less by the sectional weights. Claims if any for payment for this item shall be submitted with supporting document giving the schedule of bars with sketches. The sectional weight to be adopted shall be IS Sectional weight.

b)         Standard hooks, cranks, bends, authorized laps etc. shall be measured.

c)         Separator pieces between two or more layers of steel shall not be measured.

d)	No payment shall be made for lap welding or butt welding if permitted, Supports, chairs, hangers, etc. of height 300 mm and less, required for keeping the steel in position unless otherwise specified in the contact. For supporting horizontal reinforcement at heights larger than 300 mm, support drawings shall be prepared by the contractor and payment shall be made for the supports as approved by the Engineer-in-charge, or as actually placed, whichever is less, at the same rate as for reinforcement.

e)	No extra payment will be paid for modification of already embedded reinforcement, if required due to faulty fabrication or placement.

f)	Dowels neither shown in the drawings nor instructed by the Engineer-in-charge, but required for construction facilities and/or sequences, shall not be measured.

11.0     TECHNICAL SPECIFICATION FOR FORMWORK:

11.1   The section of the specification covers the technical requirements for furnishing form work/shuttering for plain & reinforcement concrete works for all structures all levels including buildings, foundations, trenches, tunnels, rail tracks, water storage tanks etc. as required for complete job, as per approved construction drawings under this contract.

11.1.1	If it is so desired by the Engineer-in-charge, the contractor shall prepare, before commencement of the actual work, design and drawings for formwork and centering and get them approved by the Engineer-in- charge. The formwork shall conform to the shape, lines and dimensions as shown on the drawings.

11.1.2	Materials used for the form work inclusive of the supports and centering shall be capable of withstanding the working load and remain undistorted throughout the period it is left in service.

11.1.3	Formwork shall be composed of steel and/or best quality shuttering wood of non-absorbent type. Timber shall be free from significant knots and shall be of medium grain as far as possible and hard woods shall be used as caps and wedges under or over posts. Plywood or equivalent shall be used where specified to obtain smooth surfaces, for exposed, concrete work. Struts shall generally be mild steel tubes, and strong Sal ball is 150 mm in diameter or above. Bamboos, small diameter balls, etc. shall not be used unless approved by the Engineer-in-charge in specific cases

11.1.4	Supports or props should not bear on an unproved lower suspended floor or beam unless calculations are submitted to the Engineer-in-charge to confirm the strength of the lower floor or beam and no propping shall be taken out until the Engineer-in-charge's approval has been given.

11.1.5	The centering shall be true and rigid and thoroughly braced both horizontally and diagonally. The forms shall be sufficiently strong to carry without undue deformation, the dead weight of the concrete as a liquid as well as working load.

Where the concrete is vibrated, the form work shall be strong enough to withstand the effects of vibration, without appreciable deflection, bulging, distortion or loosening of its components. The joints in the formwork shall be sufficiently tight to prevent any leakage or mortar. The formwork shall be such as to ensure a smooth uniform surface free form honeycombs, air bubbles, bulges, fins and other blemishes. Any blemish or defect founding the surface of the concrete must be brought to the notice of the Engineer-in- charge immediately and rectified free of charge as directed by him. To achieve the desired rigidity, the bolts, space blocks, the wires and clamps as approved by the Engineer-in-charge shall be used but they must in no way impair the strength of concrete or leave stains or marks on the finished surface. Where there are chances of these fixtures being embedded, only mild steel or concrete of adequate strength shall be used. Bolts passing completely through liquid retaining walls/slabs or the purpose of securing and aligning the formwork should not be used.

11.1.6	For exposed interior and exterior concrete surfaces of beams, columns and walls, plywood or other approved forms, thoroughly cleaned and tied together with approved corrosion-resistant devices shall be used. Rigid care shall be exercised in ensuring that all columns are plumb and true and thoroughly cross-braced to keep them so. All floor and beam centering shall be crowned not less than 8 mm in all directions for every 5 meters span. Unless described on the drawing or elsewhere to the contrary, beveled strips 25 mm shall be provided, without any extra charge, to form angles and in corners of columns and beam boxes for chamfering of corners. Temporary openings for cleaning, inspection and for pouring concrete shall be provided at the base of vertical forms and at other places, where they are necessary and as may be directed by the Engineer-in-charge. The temporary openings shall be so formed that they can be conveniently closed when required and must not leave any mark on the concrete.

11.1.7	All horizontal forms shall be constructed for pressures from the dead weight of concrete and embedment and a minimum live load of 200 kg/m².

11.1.8	All details of formwork, placing, tying etc. shall be subject to the approval of the Engineer and the contractor shall submit drawings, when requested, showing details of form construction. The contractor shall be responsible for the adequacy of the formwork to withstand the pressure of freshly placed concrete or other loads imposed without failure, movement or deflections of the component parts.

11.2.1. Cleaning & Treatment of Forms:

All parts of the forms shall be thoroughly cleaned of old concrete, wood shavings, saw dust, dirt and dust sticking to them before they are fixed in position. All rubbish, loose concrete, chippings, shavings, sawdust etc. shall be scrupulously removed from the interior of the forms before concrete is poured. Compressed air jet and/or water jet along with wire brushes, brooms etc. shall be used for cleaning.

The inside surface of the formwork shall be treated with approved non staining oil or other compound before it is placed in position. Care shall be taken that oil or other compound does not come in contact with reinforcing steel or construction joint surfaces and shall be non staining and non- injurious to concrete. They shall not be allowed to accumulate at the bottom of the formwork. The oiling of the formwork will be inspected just prior to placement of concrete and redone wherever necessary.

11.2.2. Design:

The formwork shall so designed and erected that the forms for slabs and the sides of beams, columns and walls are independent of the soffits of beams and can be removed without any strain to the concrete already placed or affecting the remaining formwork. Removing any props or re-propping shall not be done except with the specific approval of the Engineer and props can be reinstated in anticipation of abnormal conditions. If formwork for column is erected for the full height of the column, one side shall be left open and built up in sections, as placing of concrete progress. Wedges, spacer bolts, clamps or other suitable means shall be provided to allow accurate adjustment and alignment of the formwork and to allow it to be removed gradually without jarring the concrete.

11.2.3. Tie Rods:

Metal tie rods shall be used for supporting all forms. Provision shall be made for removal of a section of each rod at surface of the concrete to a depth of approximately 50 mm. All holes left by the removal of hital huts of other removal fixture embedded in the face of the concrete shall be filled and finished with cement in a manner specified in the section of "Finishing", threaded inserts embedded on the wall shall be used for attaching the forms to previously plated concrete.

11.2.4.Tie Wires:

Wire ties will be permitted only upon approval at the Engineer-in-charge and when permitted, shall be cut off flush with the face of the concrete, or countier sunk, filled and finished, as required by the Engineer-in-charge in the manner specified under the Sections of "Finishing".

11.2.5 Chamfers and fillets:

All corners and angles shall be formed with 45' mouldings to form chamfers or fillets on the finished concrete. The standard dimensions of chamfer and fillets, unless otherwise detailed or specified shall be 25 x 50 mm. Care shall be exercised to ensure accurate mouldings. The diagonal face of the moulding shall be planned or surfaced to the same texture as the forms to which it is attached. Unit rates quoted shall include providing the chamfers as specified or as shown on the drawings.

11.2.6 Construction joint chamfers:

Vertical construction joints on faces that will be exposed at the completion of the project shall be chamfered as above except where not permitted by the Engineer-in-charge.

11.2.7 Joints:

Joints in forms shall be horizontal or vertical unless otherwise specified and shall be sufficiently tight to prevent any leakage. Suitable devices shall be used to hold adjacent edges together in accurate alignment. All forms shall be such that they can be removed without hammering or plying against the concrete.

Inspection of Forms:

Casting of concrete shall start only after the formwork has been inspected and approved by the Engineer. The concreting shall start as early as possible within 3 (three) days after the approval of the formwork and during this period the formwork shall be kept under constant vigilance against any interference. In case of delay beyond three days, a fresh approval from the Engineer shall be obtained.

11.3.1 Removal of Forms:

Before removing any formwork, the Contractor must notify the Engineer well in advance to enable him to inspect the concrete if he so desires. The Contractor shall begin the removal of formwork only after approval of Engineer-in-charge. He shall place on record the date on which the concrete is placed in different parts of the work and the date of the removal of formwork there from. This record shall be checked and counter-signed by the Engineer-in- charge. The contractor shall be responsible for the safe removal of formwork but the Engineer-in-charge may delay the time of removal if he considers it necessary. Any work showing signs of damage through premature removal of formwork or loading shall be entirely reconstructed without any extra cost to Owner. Forms for various types of structural components shall not be removed before the minimum periods specified, which shall also be subject to the approval of the Engineer-in-charge. However, in any case, formwork shall not be struck until the concrete has reached a strength at least twice the stress to which the concrete may be subjected to at the time of removal of forms.

11.3.2.	The number of props left under their sizes and disposition shall be such as to be able   to safely carry the full dead load of the slab beam or arch as the case may be together with any live load likely to occur during curing or further construction.

11.3.3.	Where the shape of the element is such that the formwork has reentrance angles, the  form work shall be removed as soon as possible after the concrete has set, to avoid shrinkage cracking occurring due to the restraint imposed.

11.3.4.	In case of cantilever slabs the removal of forms shall begin from outer edge towards support where as in case of slabs on four sides the removal of forms shall begin from center to supports.

11.4    Tolerance for the finished concrete:

11.4.1	The formwork shall be so made as to produce a finished concrete true to shapes, lines, plumb and dimensions .Tolerances limit specified under Clause 10 of IS: 456-2000 shall be followed where so desired by the Engineer-in-charge. The Engineer-in-charge may call for finished work at any time to set standards of workmanship. Once approved these will become the acceptance sample.

The tolerance given above are specified for local aberrations in the finished concrete surface and should not be taken as tolerances for entire structure taken as a whole or for the setting and alignment of formwork, which should be as accurate as possible and true to shape required to the entire satisfaction of the Engineer-in-charge. Any error within the above tolerance limits or any other as may be specially set up by the Engineer-in-charge, if noticed in any lift of the structure after stripping of forms, shall be corrected in the subsequent work to bring back the surface of the structure to its true alignment.

11.5    Reuse of Forms:

11.5.1 Formwork may be reused, provided that it is true, un-warped, thoroughly clean and without broken or damaged edges and equal in use in every respect to a new lumber. All form lumber shall have the contact surfaces re-oiled or recoated with an approved composition prior to usage.

11.5.2	Before reuse all forms shall be thoroughly scrapped, cleaned, joints etc. examined, and when necessary repaired, and inside surface treated as specified herein before. Formwork shall not be used/reused, if de-cleared unfit or unserviceable by the Engineer-in-charge.

11.6 Classification:

Generally, the 'ordinary' class formwork shall be used unless otherwise directed by the Engineer.

a) Ordinary 	These shall be used in places where ordinary surface finish is required and shall be composed of steel and/or approved good quality partially seasoned timber.

b) Plywood 	These shall be used in exposed surfaces, where a specially good

finish is required and shall be made of approved brand of heavy quality plywood to produce a perfectly uniform and smooth surface conforming to the shape described in the drawing with required grain texture on the concrete. Reuse may only be permitted after special inspection and approval by the Engineer. He may also permit utilization of used plywood for the 'ordinary' class, if it is still in good condition.

c) Ornamental	 These shall be used where ornamental and curved surface are required and shall be made of selected best quality well seasoned timbers or of plywood, which can be shaped correctly.

d) Shell roof 	For this item, the detailed design of formwork shall be submitted to the Engineer-in-charge, well in advance for his approval. Units of shell forms may be used repeatedly but prior approval shall be required for each repetition. Extra care shall be taken to keep correct levels and profiles.

Opening, chases, grooves, rebates, block outs etc. The Contractor shall leave all openings, grooves, chases, etc. in concrete work as shown on the drawings or as specified by the Engineer.

11.7  Acceptance:

11.7.1	Finished concrete shall be true to shape, lines, levels, plumb and dimensions as shown on drawings.

11.7.2	All embedded fixtures shall be of correct type and in correct position as shown in drawings.

11.7.3	Finished concrete surfaces shall be free from blemishes like honey-combs air bubbles, fins etc.

11.7.4	Exposed decorative concrete surface shall be free from rust stains, grease and mould oil etc. and shall have uniform pleasing appearance to the satisfaction of the Engineer-in-charge.

11.7.5 The finished concrete shall be of a standard at least equal to that of the accepted sample.

12.0     AGGREGATES FOR P.C.C / R.C.C WORKS:

The aggregates required for Plain or reinforced cement concrete works should be obtained by  machine crushing ,free from dust HBG of varying sizes with the composition given below for well graded metal.

13.0     HOLD FASTS & BED BLOCKS:

Hold fasts of doors and windows are to be provided in PCC(1:2:4) using 20 mm well graded HBG metal with the composition as given above . Bed blocks are to be provided in CC (1:2:4) using 20 mm well graded HBG metal.

The quoted rate shall include cost and conveyance of all materials, SEIGNORAGE labour charges, form work, curing with all leads and lifts etc., complete for finished item of work.

14.0     CEMENT:-

Cement shall be OPC/ PPC of 43 grade / 53 grade of make like  RAASI, PRIYA, KCP, RAMCO, L&T, BIRLA or any other ISO company. Cement shall be procured by the contractor only.

i)	All cement used for the work shall be ordinary Portland cement or such other cement as may be permitted by the Engineer-in-charge. Portland cement shall comply with the requirements of the latest issue of IS 269.

ii)	Cement which has remained in bulk storage at the mill for more than 6 months, or which has remained in bags at the dealer's storage for over 3 months, or which has been stored at project site for more than 3 months shall be re-tested before use. Cement shall also be rejected if it fails to conform to any of the requirements of these specifications.

15.0	REINFORCED CEMENT CONCRETE :

15.1	Sun Shades: Sun shades of 62.5mm average thickness are to be constructed in RCC (1:2:4) using 20mm well graded machine crushed HBG metal with the composition as given above.

15.2	Lintels: Lintels are to be casted in RCC(1:2:4) nominal mix using 20mm well graded HBG metal with the composition as given above.

15.3	Under reamed Piles, Columns, Beams, Roof slab, Balcony/Portico, Projection Slab:

Under reemed Piles, Columns are to be laid with DESIGN MIX CONCRETE  RCC M20 grade using  10 to  20mm well graded HBG metal.

Reinforced cement concrete 1:2:4   for   columns, Beams. Roof slab, Balcony/Portico, Projection Slab using 10 mm to 20 mm size graded HBG machine crushed metal (50% each) from approved quarry giving cube crushing strength of 150 kg/m² and a minimum of 330 Kgs of cement for 1 m³ of concrete including cost and conveyance charges of cement and all other materials to site, scaffolding charges, seigniorage charges, centering, shuttering, machine mixing, laying concrete, curing for specified number of days by curing with wet gunny bags, vibrating etc compaction by pan vibrator or needle vibrator supplemented by hand spreading , rodding and tamping , all incidental and operational charges, all leads and lifts  and for all floors leaving gaps and pockets wherever required etc complete.,  but excluding cost of steel and its fabrication ,all incidental charges etc. complete for finished item of work as directed by the Engineer in charge.

Reinforced cement concrete 1:2:4 columns, beams, roof slab using 10mm to 20 mm size graded HBG machine crushed metal (50% each) from approved quarry giving cube crushing strength of 150 kg/m² and a minimum of 330 kg of cement for 1 m³ of concrete including cost and conveyance charges of cement and all other materials to site, scaffolding charges, seigniorage charges, centering, shuttering, machine mixing, laying concrete, curing for specified number of days by curing with wet gunny bags, vibrating etc compaction by pan vibrator or needle vibrator supplemented by hand spreading , rodding and tamping , all incidental and operational charges, all leads and lifts  and for all floors leaving gaps and pockets wherever required etc complete.,  but excluding cost of steel and its fabrication ,all incidental charges etc. complete for finished item of work as directed by the Engineer in charge.

16.0	CONCRETING:-

16.1   Composition:	 Concrete shall be composed of cement, river sand also termed as/fine

aggregate  broken rock or coarse aggregate and water, all machine mixed and brought to proper consistency whenever so ordered by the  Executive Engineer/ Civil/ Gr.Hyderbad, Admixtures shall be added as stated in the special conditions. The exact proportion of each type of aggregate listed in these specifications will be determined from time to time on the mechanical analysis of the aggregate stock piles and tests of resulting concrete test cubes, or cylinders. In general, the design mix proportions are adjusted to produce a durable plastic and workable concrete suitable for the specific conditions of placement and design strength. The specifications for the cement, sand, coarse aggregate and water have been detailed in Technical specifications. (IN situ mix test for cement, aggregates shall conducted for cement concrete exceeding 100 m³ or 17 hours)

16.2	Concreting :-	The contractor’s rate for various items of work shall include cost of materials, seigniorage, conveyance, labour, leads & lifts etc. complete. Concreting work, reinforcements, shuttering including curing etc. should generally conform to the relevant specifications as per ISI except for deviation if any hereunder. The strength requirements of concrete proposed to be used for various items of work mentioned in the bill of quantities shall be as follows.

Table

-------------------------------------------------------------------------------------------

Compressive Works test strength in N/sq.mm on 150 mm  after testing conducted in

accordance with IS :517 Grade of

------------------------------------------------------------------------------------------------

Concrete	                 Min. at 7 days 	                Min. at 28 days

------------------------------------------------------------------------------------------------

M 10			7.0		              	10

M 15			10.0				15

M 20			13.5				20

M 25			17.0				25

M 30			20.0				30

M 35			23.5				35

M 40			27.0				40

M 45			30.0				45

M 50			33.5				50

------------------------------------------------------------------------------------------------

Note: Cylinder strength.

Where compressive strength tests of cylinders are adopted the compressive strength given above for cubes shall be modified according to the formulae.

Maximum cylinder compressive strength } 0.8 x compressive strength specified

required					  }	for 15cm cubes.

The approximate quantities of materials in dry conditions required for obtaining M20 grade concrete for 1 cum are as follows:

---------------------------------------------------------------------------------------------------------

Sl.No.	Grade of concrete	Sand in Cum	Coarse aggregate	Min cement

in m³.			per 1m³

of concrete.

---------------------------------------------------------------------------------------------------------

1.		M20		0.46			0.92		330 Kgs.

2                      M25                0.46                             0.92                 360 Kgs.

---------------------------------------------------------------------------------------------------------

Any deviation in cement content (increase) from those specified in the above table over that required as per design mix shall be to the account of Board. No extra payment or deduction shall be made for variation in several ingredients except the cement content.

16.3 	Sampling: -Sampling of fine and coarse aggregate and cement will be done periodically in accordance with standard practice/ cement concrete exceeding 100 cum or 17 hours, and tests made under the supervision of the quality control Engineer. Also the routine tests shall be made in various stages of batching Operation  section for which the contractor shall provide all facilities necessary for procurement of representative samples for which no payment shall be made.

16.4	Slump tests: -	All slump tests be made in accordance with recommended procedure given IS code 1199-1959 for reinforced concrete (setout Granville and Thomas or in designation C.148,52 of the American society of testing materials. The slump preferred to, shall be determined when the concrete is about to be deposited as such less slumps within the limits will be required as may, in the opinion of the  Executive Engineer/ Civil/ Gr.Hyderbad , be practicable to produce concrete of better quality and of greater economy. Greater slump (but in all cases limited to 6” (15cm) maximum than those specified in the table) will be permitted in exceptional cases, wherein the opinion of the Executive Engineer/ Civil/ Gr.Hyderbad , internal vibration of the concrete is not practicable and where especially authorize by the  Executive Engineer/ Civil/ Gr.Hyderbad for concrete in position, especially difficult for placement as in thin or heavily reinforced section.

16.5    Strength:-The required strength mentioned in the table are minimum crushing strength of ‘work test’ cylinders that must be obtained on cylinders made from concrete, either at the batching plant or at the placing point, and standard cured. The 28 days strength is the average strength of 3 test specimen taken from a single batch provided that not more than 10% of specimens tested shall have strength less than 80% of the required strength. The average strength of all tests for a given period shall equal or exceed the required strength. If the average crushing strength is higher, the contractor shall not be entitled to any increase in payment of work on account of the actual strength being above the minimum specified. In addition to the 28 days strength tests, the  Executive Engineer/ Civil/ Gr.Hyderbad may at his discretion make 7 days strength tests. The minimum 7 days strength realized will not normally be less than 2/GROUND of the minimum 28days strength specified. The exact relation will be fixed on the site after studying the actual values realized. If at any time, the 7 days strength indicate that the strength of 28 days may not be achieved, as specified the  Executive Engineer/ Civil/ Gr.Hyderbad shall have the authority to suspend concreting operations, until the reasons have been investigates and corrected and/or the mix has been redesigned etc and the contractor shall comply herewith without such suspension being made a reason for any claim.

The concrete for testing shall be collected as it comes out of the mixer once or more often as the  Executive Engineer/ Civil/ Gr.Hyderbad may direct, and in quantity sufficient to prepare at least 3 test pieces from each sample. The compressive strength of concrete shall be determined through the medium of tests of (15x30cm) cylinders. If cylinders are made they shall be made and cured in accordance with American society of testing materials, designation C.31-40 and tested in accordance with designation c.31-49. Cylinders 6” by 12” will be used for concrete made from aggregate and smaller.

In addition to the strength tests carried above it is contemplated that the tests on actual cores from the concrete laid in position shall be made, and results thereof shall not be in any case lower than those of the test pieces. If the cores taken out show unreasonably low results the work is liable to be rejected and may be required to be dismantled and redone with all consequences to the contractor. The tests shall be carried out by the TSSPDCL at its own cost and as directed by the  Executive Engineer/ Civil/ Gr.Hyderbad and the contractor shall afford all reasonable facilities for taking the test cores.

The contractor shall also arrange to fill the test holes left by the removal of the cores with concrete of the required strength without any extra payment and to the satisfaction of the  Executive Engineer/ Civil/ Gr.Hyderbad .

The contractor shall at all times have access to and associate with sampling, design and tests of trial mixes, tests of strengths and similar other Operations. It shall then be the contractor’s responsibility to rebooting on the works, concrete of quality, density and strength corresponding to the laboratory and test designs.

The laboratory mix will be so designed that the minimum strength achieved on the laboratory test cylinder is about 25% higher than that specified above that concrete has a density of (155lbs) per cubic ft or more (2486 kg/m3) and as impermeable as can be made. The same mix shall be used in the field to assure the achievement of quality specified.

Failure on the part of the contractor to associate with the Operations aforesaid shall not absolve him of the responsibility of producing on the works concrete of specified quality, density and strength with design mixes determined from laboratory tests and results.

16.6	Water cement Ratio: -The water cement ration will be regulated by the requirements of workability and design, but in general will not exceed 0.60 by weight, exclusive of water absorbed by the aggregates. The amount of water shall be adjusted for any variation in the moisture content or the grading of the aggregate as they enter the mixer in any batch and shall not be more than the minimum necessary to produce concrete of the required consistency after making period specified in general or from time to time. Uniformity shall be maintained in the consistency of concrete from batch to batch.

16.7	Proportioning of concrete: -	The exact proportions in which the different gradients are to be used from the different parts, of the work shall be determined by the contractor in any one of the recognized laboratories under the supervision of the departmental staff after trial mixes, the structural concrete is to be commenced only after establishing the cement in each grade of mix as per IS 456. The cost on account of laboratory test shall be to the account of the contractor.

16.8	Cement content: - The cement content is specified as the specific weight of cement used in the manufacture on 1 cum of concrete as measured in the finished work after vibration, consolidation, setting and curing. The actual volume of different gradients that would go in. in a batch of concrete to produce the specified volumetric unit shall be determined by tests and the cement content specified shall be put in for each batch supposed to produce the same unit of concrete in place is determined by the tests.

Any variation in the cement content shall also be similarly treated. No extra payment or deductions shall be made for variations in the several in-gradients except in cement content, which shall be adjusted as described. Variations in proportions of crushed metal and natural sand will not be considered for purposes of price variation.

If for any reasons it is found necessary to resort to volumetric batching instead of weigh batching which shall be subject to the specific approval of the  Executive Engineer/ Civil/ Gr.Hyderbad . The proportion of cement (by volume) to that of the various aggregates also by volume shall be so adjusted that the cement content in the specific volumetric unit of finished concrete, shall not be less than that specified for the relevant class of concrete. For this purpose one bag of cement as supplied by cement manufactures shall be taken as 1.225 cft or 50 kgs.

16.9	Variation in Cement content: - The unit rate accepted for concrete shall be adjusted to account for the increase in the quantity of cement actually designed and specified (if different from that specified in the specifications) at the same issue rate per tonne of cement i.e 2400/- per MT. The variation in the quantities of other aggregates shall not be considered as justification for price adjustment. The proportions of cement as that in the mix shall be related to the volume of the finished concrete.

16.10	Admixtures: -	The Executive Engineer/ Civil/ Gr.Hyderbad shall have the authority at any time, and from time to time to order the addition of any air entraining agent or other admixtures, to any mix of concrete in such proportion or quantity or mode, as he may specify and the contractor shall comply with the same. The admixtures shall be supplied by department free of cost for the purpose of the concrete or the motor as the case may be. The resulting modifications, if any to the content or proportion of cement as a consequence thereof, shall be accounted for in the rates for payment according to para 13.9 herein above.

The Executive Engineer/ Civil/ Gr.Hyderbad shall have the authority to arrange for the supply of the admixtures or admixtures aforesaid, through the contractor (by mutual agreement) or by other agency, as the  Executive Engineer/ Civil/ Gr.Hyderbad may deem fit. Should the mixing entail any additional expenditure to the contractor by way of additional plant, equipment, or operation, the same shall be paid for at actual cost, as may be determined by the  Executive Engineer/ Civil/ Gr.Hyderbad whose decision shall be final and binding upon the contractor.

The contractor shall not, without the written consent of the  Executive Engineer/ Civil/ Gr.Hyderbad , add any admixtures, to any mix of concrete and whenever such an admixtures is permitted, the  Executive Engineer/ Civil/ Gr.Hyderbad shall determine the adjustment in price if any, that should be made in consequence. The decision of the  Executive Engineer/ Civil/ Gr.Hyderbad shall be final an binding on the contractor.

16.11	Handling of aggregate: - The contractor shall at all times, maintain a live storage of all grades of aggregates of at least one week’s requirement of work.

16.12	Batching equipment: -The batching plant shall be of the requisite capacity to maintain the specified progress on different items of work.

16.13	Check tests for equipment’s:- The tests shall be made in the presence of TSSPDCL representatives and shall be adequate to prove the accuracy of the measuring devices. Unless otherwise directed, tests shall be made once in two weeks in the case of all other scales. The contractor shall make such adjustments, repairs or replacements s may be necessary to meet the specified requirements for accuracy of measurements.

Detailed drawings showing reinforcement details will be supplied by the  department during the course of execution. The top of roof slab of last floor is Provided with Impervious coat over exposed RCC Roof slab surfaces to required slopes with Polymer Acrylic Water Proofing layer of approved make as per manufacturer's specifications and over the layer 25 mm average thickness of screed cement concrete in CC 1:2:4 using 6 mm coarse aggregate with mixing of integral water proofing chemical at 150 ml per 50 kg of cement and over the screed concrete 4mm thick neat coat of cement plaster in CM 1:4 with mixing of integral water          proofing chemical of approved make at 150 ml per 50 kg of cement and thread lining of regular intervals of 45 x 45 cms including and cost and conveyance of all materials, water, all labour charges, chemicals, curing for specified number of days, rounding off junctions of wall and slab, all leads, lifts, heights, levels and floors etc. complete as directed by the engineer-in-charge for finished item of work.

All materials shall conform to standard specification, IS and are to be approved by the Engineer-in-charge prior to their usage in the work. For this purpose, the contractor shall whenever called up to do so, furnish samples of materials in adequate quantities and carryout all tests on materials and concrete specimens. Testing shall be done in close liaison with Engineer-in-charge or his representative and methods of test shall conform to the relevant IS Specification. Test results also shall conform to the IS Specification. The cost of samples and testing shall be borne by the contractor.

No concrete work shall be done in the absence of the Engineer-in-charge. Before placing the concrete, the Engineer-in-charge shall have inspected and approved all reinforcement in place, form work, centering and scaffolding for concrete. At least 24 hours notice shall be given for this purpose.

All concrete works shall be machine mixed, vibrated for proper compacting unless otherwise specified by Engineer-in-charge.

Transportation and placing methods and adequacy of equipment and procedure shall be studied in advance. All form work, reinforcement steel and location and details of embedded parts etc. shall be checked and approved by the Engineer-in-charge. Construction joints shall be made at only those positions shown on the drawing or at locations approved by the Engineer-in-charge.

All sleeves, inserts, anchors and embedded items required for adjacent work or for its supports shall be placed prior to concreting. Care shall be taken not to displace reinforcement and embedded parts during the placing and compaction of concrete.

Curing of concrete shall start after 8 hours of placement, and in hot weather with in 4 hours of placement in exposed faces, and kept continuously wet preferably by continuous spraying of water after the final set for a period of at least 10 days from the date of casting.

If the temperature of atmosphere during the period has been continuously above 100 C, When the temperatures are higher, the Engineer may extend the curing period for a suitably longer period.

The quoted rate for concrete shall include the supply of materials, labour, tools and tackle, plant and equipment, scaffolding, staging, form work, centering and shuttering, curing, leads and lifts, other incidental charges etc. complete for finished item of work. The quoted rate shall also include, wherever applicable, the cost of placing, keeping in position any embedment or inserts, openings, joints etc., as shown in the drawings and as directed by the Engineer-in-charge. Reinforcement steel and its fabrication shall be paid separately. The quoted rate shall be excluding basic cost of cement, required cement will be issued at department stores at free of cost.

16.14   Transport, Placing and Compaction of Concrete

The method of transporting and placing concrete shall be approved by the Engineer-in-Charge. Concrete shall be transported and placed such that no contamination, segregation or loss of its constituent materials takes place.

No concrete shall be placed in any part of the structure until the approval of the Engineer-in-Charge has been obtained in writing.

If concreting is not started within 24 hours of the approval being given, it shall have to be obtained again from the Engineer-in-Charge. Concreting shall then proceed continuously over the area between construction joints. Fresh concrete shall not be placed against concrete, which has been in position for more than 30 minutes unless a proper construction joint is formed.

Concrete when deposited shall have a temperature of not less than 4.5 dig C and not more than 38 dig. C unless otherwise specified. It shall be compacted in its final position within 30 minutes of its discharge from the mixer unless carried on properly designed agitators, operating continuously, in which case this time shall be within 2 hours of the addition of cement to the mix and within 30. Except where otherwise agreed to by the Engineer-in-charge, concrete shall be deposited in horizontal layers to a compacted depth of not more than 0.45 m when internal vibrators are used and not exceeding 0.30 m in all other cases.

Unless otherwise agreed to by the Engineer-in-charge, concrete shall not be dropped into place from a height exceeding 2 meters. When trucking or chutes are used, they shall be kept clean and used in such a way as to avoid segregation.

When concreting has to be resumed on a surface which has hardened, it shall be roughened, swept clean, thoroughly wetted and covered with a 15 mm thick layer of mortar composed of cement and sand in the same ratio as in the concrete mix itself. This 15 mm layer of mortar bed shall freshly mixed and placed immediately before placing of new concrete.

Where concrete has not fully hardened, all laitance shall be removed by scrubbing the wet surface with wire or bristle brushes, care being taken to avoid dislodgment of any particles of coarse aggregate. The surface shall then be thoroughly wetted, all free water removed, and then coated with neat cement Ground. The first layer of concrete to be placed on this surface shall not exceed 150 mm in thickness, and shall be well rammed against old work, particular attention being given to corners and close spots.

All concrete shall be compacted to produce a dense homogeneous mass with the assistance of vibrators. Where vibrators cannot be used, an alternate scheme of compaction shall be approved by the Engineer-in-charge. Sufficient vibrators, in serviceable condition, shall be kept at site so that spare equipment is always available in the event of breakdowns.

The performance requirements of vibrators shall conform to relevant IS Codes. Vibration shall not be applied through reinforcement, and where vibrators of the immersion type are used contact with reinforcement and all inserts shall be avoided as far as practicable.

16.15   Finishing

General

Immediately after the removal of forms, all exposed bars or bolts passing through the reinforced cement concrete member and used for shuttering or any other purpose shall be cut inside the reinforced cement concrete  member to a depth of at least 25 mm below the surface of the concrete and the resulting holes be closed by cement mortar. All fins caused by form joints shall be broken. All cavities produced by the removal of the firm ties, all holes and depressions, honey-comb spots, broken edges or corners and all other defects shall be thoroughly cleaned, saturated with water and carefully pointed and  rendered true with mortar of cement and fine aggregate mixed in the proportions used in the grade of concrete that is being finished use. Considerable pressure shall be applied in filling and pointing to ensure thorough filling in all voids. Surfaces, which have been filled/pointed, shall be kept moist for a period of twenty-four hours. Any repair and rectification of defective work is to be undertaken and carried out as directed by the Engineer-in-Charged and the cost is to be borne by the CONTRACTOR.

If rock pockets/honey-combs, in the opinion of the Engineer-in-charge, are of such an extent or character as to effect the strength of the structure materially  or to endanger the life of the steel reinforcement, he may declare the concrete defective and require the removal and replacement of the affected portions of the structure.

All construction and expansion joints in the completed work shall be left carefully tooled and free from any mortar and concrete. Expansion joint filler shall be left exposed for its full length with clean and true edges.

Curing of the surface shall be continued for a period as approved by the consultants.

16.16 	Classes of Finishing

The surface finishes for formed and unformed surfaces are classified and defined as below. Surface irregularities permitted for the various classes of finishes are termed either abrupt-or-gradual-. Fins or offsets caused by displaced or misplaced form sheeting, lining or form sections by loose knots in form timber or by otherwise defective from timber are considered abrupt irregularities. All other cases are described as gradual irregularities. Gradual irregularities will be measured with a template for equivalent for curved surfaces. The length of template for testing gradual irregularities on formed surfaces shall be 1.5 m in length, the permissible gradual irregularities being measured over this length of the template.

16.17    Finish for foundations and plinth

Class F2 Finish shall be obtained by the use of properly designed forms, either close jointed wrought timber forms or with forms having plywood or steel sheet lining. The abrupt irregularities shall not exceed 5mm and gradual irregularities shall be less than 8mm. Small blemishes caused by entrapped air or water may be permitted but the surface shall be generally free from honeycombing, voids and large blemishes. Surface irregularities in excess of those stipulated shall be removed by clipping or rubbing abrasive stone.

16.18   Class F3 Finish

Class F3 finish shall be formed by specially designed clothes jointed rigid forms having lining of high quality form plywood. The surface irregularities shall be limited to nil for abrupt irregularities and 3mm for gradual irregularities. Class F3 finish may be obtained form class F2 finish by carefully removing all abrupt irregularities including fins and projections by rubbing/grinding.

16.19 	Finish for floor slabs

This is the screeded finish used on surfaces over which other finishes such as wearing coats etc. are to be placed. It is also the first step in the formation of U2 and U3 finishes. The finishing operation consists of leveling and screeding the concrete to produce an even and uniform surface so that the gradual irregularities are not greater than 6mm.

Surplus concrete should be removed immediately after consolidation by striking it of with a sawing motion of a straight edge or template across a wooden or metal strip that has been set as a guide. Unless the drawings specify a horizontal surface or show the slope required, the tops of narrow surfaces, such as stair treads, walls, curbs and parapets shall be sloped approximately 10 mm per 300 mm width. Surfaces to be covered with concrete topping, terrazzo, and similar surfaces shall be smooth screeded and leveled to produce even surfaces, irregularities not exceeding 6 mm.

16.20   Construction Joints:

Concreting shall be carried out continuously up to the construction joints, the position and details of which shall be as shown on approved drawings or as directed by the Engineer-in-charge. Such joints shall, however, be kept to the minimum. For vertical construction joint, a stopping board shall be fixed previously at the pre-determined position and shall be properly stayed for sufficient lateral rigidity to pack against it. Concreting shall be continued right upto the board. The board shall not be removed before the expiry of the specified period for removal of vertical forms. Before resuming work at the construction joint where the concrete has not yet fully hardened, all laitance shall be removed thoroughly. Care being taken to avoid dislodgement of coarse aggregates. When work has to be resumed on a surface, which has hardened, the surface shall be thoroughly hacked, swept clean, wetted and covered with a layer of neat cement grout.

The neat cement grout shall be followed by a 15mm thick layer of mortar mixed in the same proportion as in the concrete and concreting resumed immediately thereafter. The first batch of concrete shall be rammed against the old work to avoid formation of any stone pockets, particular attention being paid to corners and close spots.

In all cases, the position and detailed arrangement of all construction joints shall be predetermined and got approved by the Engineer-in-charge.

16.21 Tests and Standards of Acceptance

16.22 Preliminary Tests for Designing Concrete

For designing concrete preliminary tests referred to in paras 2.0 and 3.0 shall consist of three sets of separate tests, and in each set, tests shall be conducted on six specimens. Not more than one set of six specimens shall be made on any particular day. Of the six specimens in each set, three shall be tested at seven days and the remaining three at 28 days. The preliminary tests of 7 days are intended only to indicate the strength likely to be attained at 28 days.

16.23  Work strength Tests for design concrete mix

Works strength tests shall be made in accordance with IS 517. Each test shall be conducted on ten specimens, five of which shall be tested at seven days and the remaining five at 28 days. The cubes shall be made at the rate of one set for every          50 cum., the number of cubes can be reduced to six with the specific permission of the Engineer-in-charge.

Similar works tests shall be carried out whenever the quality and grading of materials is changed irrespective of the quantity of concrete poured. The number of specimens may be suitably increased as deemed necessary by Engineer-in-charge, when procedure of test given above reveals a poor quality of concrete and in other special cases.

All work shall be carried out under the supervision of a qualified and a competent Engineer who will supervise proportioning, placing and compacting of concrete at all stages.

All necessary labour, materials, equipment, etc., for sampling, preparing test cubes, curing etc., shall be provided by the CONTRACTOR. Testing of the materials and concrete may be arranged by the Engineer-in-charge in an approved laboratory at the cost of the CONTRACTOR.

16.24 	Standard of Acceptance

The average strength of the group of cubes cast for each day shall not be less than the specified works cube strength. 20 percent of the cubes cast for each day may have values less than the specified strength, provided the lowest value is not less than 85 per cent of specified strength.

16.25 	Manufacturer’s Certification: Testing Results etc.

For all materials required for concrete construction including cement, aggregate, water, reinforcement the original copies of test certificates,  test results etc., either carried out by the manufacturers or any other agency, the mix design recommendations etc. shall be submitted to Engineer-in-charge for his approval and record which shall remain the property of the owners.

16.26 	Chloride contents

Since the chloride contents of the constituent materials of the concrete would be additive, it is desirable to keep a check on the overall chloride content of the concrete to keep it minimal. The cost of the testing for chloride content of the ingredients of concrete and of undertaking remedial measures if the chloride content is more than the permissible limit shall be borne by the CONTRACTOR.

Surface of prepared voids shall be wetted for 24 hours immediately before the patching material is placed. Repair of concrete shall be made by skilled workmen. Repairs shall be made as soon as practicable after removal of forms and in a manner to meet the requirements for the finish specified for particular location.

For repair of the concrete works, the CONTRACTOR may use epoxy of approved agency as a bonding agent prior to placing fresh concrete. The use or otherwise of epoxy for the repair work will be at discretion of the Engineer-in-charge. Epoxies shall be applied in strict accordance with the instructions of the manufacturer.

Epoxy is a two packed or three packed system containing base and hardener/s. The shelf life of the unmixed cans is about one year or more when stored in a place where ambient temperature does not increase beyond 24 degrees centigrade. The base and hardener/s shall be mixed in correct proportions recommended by the manufacturer. The blend after mixing intimately shall have a pot life of one hour and the material shall be applied over the old concrete to form a thin film. Fresh concrete shall be deposited immediately prior to the film drying up so as to ensure proper bonding between both concretes.

Where the dry pack method is used, holes shall be sharp and square at surface edges, but corners within holes shall be rounded. The perimeter of the hole shall be under-cut in several places. Holes for dry pack shall have a minimum depth of 25 mm. The holes to be repaired shall be scrupulously clean and slightly wet with no free water on the surface. The surface shall be then dusted slightly with cement by means of dry brush. Under no conditions shall the holes be painted with neat cement grout.

The dry pack mix shall be proportioned by weight: 1 part cement to 2.5 parts of sand that will pass a No.17 screen. Only enough water shall be used to produce a mortar which will stick together when moulded into a ball by a slight will stick together when moulded into a ball by a slight pressure of hands and will not extrude water but will leave the hands just damp. Dry pack material shall be placed and packed in layers having a compacted thickness of about 10mm. Each layer shall be solidly compacted over its entire surface by use of hardwood stick and hammer. The stick is normally about 300mm to 460mm long and not over 30mm in diameter. Most of the tamping should be directed at a slight angle and towards the side of the hole to assure maximum compaction and bond. Water shall not be used to facilitate finishing.

Filling materials used in repair of surfaces which will be exposed after completion of the project shall be made with cement from the same source as that used in concrete and blended with sufficient amount of white portland cement to produce the same colour as in adjoining concrete. Patched surface shall be given a final treatment of the patch to match that of the surrounding material.

Immediately after patching is completed, the patched area shall be covered with approved non staining, water-Saturated material and shall be kept wet and protected against sun and wind for a period of 12 hours. Thereafter, the patched area shall be kept continuously wet by a fine spray or sprinkling of water for not less than 10 days as required under section 9.1 and 11.1 of this specification. The layers of unite may be reinforced with steel mesh if directed by the Engineer-in-charge.

The extent of repair shall be decided upon by the Engineer-in-charge. The cost of repairs of defective areas shall be borne by the CONTRACTOR. The Engineer-in-charge may adopt at his discretion any other method of repairing like grouting with cement grout, epoxy grout or guniting etc., which will be carried out by the CONTRACTOR at his cost as per the specifications supplied by the Engineer-in-charge.

16.27    sampling & testing :

16.27.1    General

The contractor shall carry out all sampling and testing in accordance with the relevant Indian Standards and as supplemented herein for the following items at his own cost unless otherwise specified in this specification. The Contractor shall get the specimens tested in a laboratory approved by the Engineer and submit to the Engineer the test results in triplicate within 3 (three) days after completion of the test.

16.27.2      Aggregate

The Contractor shall carry out any or all the tests aggregates as may be required by the Engineer in accordance with IS:2386 Part I to VIII. The acceptance criteria of the samples tested shall be in accordance with the requirements of the relevant Indian Standards.

16.27.3       Water

Sampling and Testing of water being used for concrete works as per IS:3550 will be carried out by the Contractor at regular intervals and whenever directed by the Engineer. The final acceptance criteria in case of doubt will be as per IS:3025 & IS:456.

16.27.4       Admixture

16.27.5     a)  Air Entraining Agents

Initially, before starting to use A.E.A., relationship between the percentage of air entrained and the cylinder cube crushing strength vis-à-vis quantity of A.E.A. used for all types of concrete will be established by the Contractor free of charge by carrying out sufficiently large number of tests. After that, at regular intervals and whenever directed by the Engineer, the Contractor will check up free of charge, the actual percentages of air entrained and corresponding crushing strengths to correlate with the earlier test results.

b)  Other Admixtures

Tests for establishing the various properties of any other admixtures which may be required to be added shall be carried out by the Contractor free of charge to the Purchaser.

16.27.6      Concrete

The sampling of concrete, making the test specimens, curing and testing procedure etc. shall be in accordance with IS:517 and IS:1199 the size of specimen being 15 cm cubes. Normally, only compression tests shall be performed but under special circumstances the Engineer may require other tests to be performed in accordance    with IS:517. Sampling procedure, frequency of sampling and test specimen shall conform to Clause 14 of IS:456. To control the consistency of concrete from every mixing plant, slump tests and/or compacting factor tests in accordance with IS:1199 and as mentioned in of this specification shall be carried out by the Contractor every two hours or as directed by the Engineer. Slumps corresponding to the test specimens shall be recorded for reference.

The acceptance criteria of concrete shall be in accordance with Clause 15 of IS:456. However, in exceptional circumstances, the Engineer may, at his discretion, accept a concrete of lower strength than specified and which is otherwise acceptable according to IS:456. Concrete work found unsuitable for acceptance shall have to be dismantled and replacement is to be done as per specification by the Contractor. No payment for the dismantled concrete, the relevant formwork and reinforcement, embedded fixtures, etc. wasted in the dismantled portion shall be made. In the course of dismantling, if any damage is done to the embedded items or adjacent structures, the same shall be made good, free of charge by the Contractor, to the satisfaction of the Engineer.

  - The Bar Bending Schedule with the necessary hooks, laps, spacers and chairs shall be 100% checked for all foundation concreting before start of work:

  - Cutting tolerances for bars shall be as follows:

a) When the specified length is not				 = 25 mm

stated to be either maximum or 			              +75 mm

minimum.

b) When the minimum length is specified                           	+ 75 mm

c) When the maximum length is specified                            	 = 50 mm

  - All the bent bars shall be checked as per approved Bar Bending Schedules, unless otherwise specified by the Engineer-in-charge, reinforcement shall be placed within the following tolerances:

Tolerance

a) For member with effective                                      + 10 mm

depth 200 mm or less

b) For member with effective                                     + 15 mm

depth more than 200 mm

The cover shall in no case be reduced by more than one third of specified cover or 5 mm whichever is less. Also, in no case shall the cover be increased by more than 10 mm.

All the joints and crossing of bars shall be checked to see that they are

tied  properly with annealed wire as per specification.

Any of the bars selected for use shall be free from cracks, surface flows,    laminations and rough, jagged and imperfect edges.

After the reinforcement cage has been put in proper position and tied

with the main bars.

Tolerance in the foundation Blocks/Bolts for steel structures:

i) 	Along the depth                                      		+ 5 mm

ii) 	Along the slope                                       		1/1000

iii)	 Permissible deviation of anchor bolts (Plan view):

a) Located within the                           		  5 mm

contour of column base

b)    Located outside the                              10 mm

contour of column base

iv) 	Permissible deviation in                  		 	+ 20 to 0 mm

level of anchor bolts

v) 	Deviation of anchor bolt                  			+ 30 to 0 mm

thread length.

16.27.7       Acceptance Criteria:

16.27.7.1    General:

The contractor shall carry out all sampling and testing in accordance with the relevant Indian Standards at his own cost, in a laboratory approved by the Engineer-in-charge, and submitting of the test.

16.27.7.2     Testing of concrete:

- Normally, only compression tests shall be performed but the Engineer-in-charge may require other test to be performed in accordance with IS:517 (latest edition).

- For each grade of concrete as follows:

-----------------------------------------------------------------------------------------------

Quantity of concrete 				Number of samples

in the work, cu.m.

------------------------------------------------------------------------------------------------

  - 1

  - 2

  - 3

  - 4

51 & above                                                            4  plus one additional for each  additional 50 m³ part thereof.

-----------------------------------------------------------------------------------------------

However at least one sample shall be taken from each shift. At least 6 (six) specimens per sample shall be taken and 3 (three) of these shall be tested at 7 (seven) days and remaining at 28 days. Minimum compressive strength of 15 cm cubes of different grades of concrete at 7 days shall be as per table 5 of IS: 456-2000

.

- To control the consistency of the concrete from every mixing plant, slump tests and/compaction factor tests in accordance with IS:1199 shall be carried out by the contractor every two hours or as directed by the Engineer-in-charge. Slumps corresponding to the test specimens shall be recorded for reference. The Engineer-in-charge, at his discretion, may waive the above tests for small and unimportant concreting.

16.27.7.3 ACCEPTANCE CRITERIA FOR CONCRETE

- The acceptance criteria of concrete shall be in accordance with IS: 456 (latest edition).

- Concrete work found unsuitable for acceptance shall have to be dismantled and replacement is to be done as per specification by the contractor. No payment shall be done for the dismantled concrete, the relevant formwork and reinforcement, embedded fixtures, etc. wasted in the dismantle. If any damage is done to the embedded items or adjacent structures, the same shall be made good, free of charge by contractor, to the satisfaction of Engineer-in charge.

- The dimensions of concrete as cast when compared with those on the drawing shall be within the tolerances given below; steps in surface alignment shall not exceed    2 mm.

No reduction will be permitted in the cover to reinforcement because of a specified negative tolerance in a concrete section.

STRUCTURAL ELEMENT 			PERMISSIBLE

DETAIL                                                               DEVIATION IN MM

Faces of concrete in foundations and 		+25                    -5

structural members against which

backfill is placed

Exposed concrete in foundations  			+10                     -5

Top surfaces of slabs and of concrete		+10                     -5

to received grouted plant or structural

steel work

Alignment of beams, columns, walls, 		+ 5                       -5

slabs & similar items.

Cross sectional  dimensions of beams,            	+ 5                       -5

columns, walls, slabs and similar items.

Level and alignment of holding down         	 + 5                      -5

Bolts.

Level of holding-down bolt assemblies	 	+10                     -5

Alignment of holding-down bolt	        		+ 5                      -5

Assemblies.

Centers of pockets or holes with greatest 		+ 5                     -5

lateral dimension not exceeding 150 mm.

Centers of pockets or holes with greatest 		+10                     –5

lateral dimension exceeding 150 mm

Departure from alignment in roads and 	  	+15                      -5

paved areas

Top surface of roads and paved areas	   	+ 5                       -5

Plumb  1 in 1000 of height.

16.27.7.4        STANDARD DEVIATION

Standard deviation shall be based on test results and determination of Standard deviation shall conform to Clause 14.5 of IS:456.

16.27.7.5        INSPECTION AND CORE TESTS

Inspection of concrete work immediately after stripping the formwork and core test of structures shall conform to Clause 17 of IS:456.

16.27.7.6       LOAD TEST

Load Tests of structural members may be required by the Engineer, when the strength of test specimen results fall below the required strength, as per 'Load Test on Parts of Structures'. Clause 17.5 of IS:456. If load testing is decided by the Engineer, the member under consideration shall be subjected to a test load equal to 1.25 (one and a quarter) times the specified live load used for design and this load shall be maintained for a period of 24 (twenty four) hours before removal. The detailed procedure of the test is to be decided by the Engineer. Load tests shall not be made until the structure is at least 56 days old.

If the member shows evident failure, such changes as are necessary to make the structure adequately strong shall be made by the Contractor free of cost to the Owner. Alternatively, if permitted under Statutory Regulations and at the discretion of the Engineer, the structure under test or a portion thereof may be retained as such without any modification by de-rating its load bearing capacity, provided the design criteria allows such de-rating. A reinforced concrete beam, floor or roof shall be deemed to have passed the test if the maximum deflection at the end of 24 hours does not exceed the deflection given in Clause 17.5 of IS:456. The entire cost of load testing shall be borne by the Contractor. If a portion of the structure is found to be unacceptable, it shall be dismantled and replaced by a new structure as per specification. The entire cost of dismantling and replacement and restoration of the site being borne by the Contractor. If, in the course of dismantling, any damage is done to the embedded items and or other adjacent structures, the same will be made good, free of charge by the Contractor to the satisfaction of the Engineer.

16.27.7.7   LIST OF IS CODES AND STANDARDS FOR REFERENCE:

All work under this specification shall, unless specified otherwise, conform to the latest revisions and/or replacements of the following or any other Indian Standard Specifications and Codes of Practice. In case any particular aspect of work is not specifically covered by Indian Standard Specifications, any other standard practice, as may be specified by the Engineer, shall be followed:-

IS:73 		Indian Standard Specification for Paving Bitumen

IS:217		Indian Standard Specification for Coal Tar Pitch

IS:226		Indian Standard Specification for Structural Steel (Standard quality)

IS:269		Indian Standard Specification for Ordinary and Low Heat Portland Cement

IS:383	            Indian Standard Specification for Coarse and Pine Aggregates from

Natural  Sources for concrete

IS:432              Indian Standard Specification for Mild Steel and Medium Tensile

Steel Bars  and Hard Drawn Steel Wire for concrete reinforcement

IS:455 		Indian Standard Specification for Slab Cement

IS:456 		Indian Standard Code of Practice for Plain and reinforced concrete

IS:457 		Indian Standard Code of Practice for general construction of plain

and reinforced concrete for Dams and other Massive Structures

IS:517 		Indian Standard Specification for methods of test for strength of Concrete

IS:1139 	Indian Standard Specification for hot rolled mild steel and medium

tensile steel and high yield strength steel deformed bars for concrete reinforcement

IS:1199 	Indian Standard Specification for methods of sampling and analysis of Concrete

IS:1200 	Indian Standard Specification for method of Part II measurement

cement concrete  works

IS:1200 	Indian Standard Specification for method of Part V measurement of Formwork

IS:1322 	Indian Standard Specification for Bitumen Felts for waterproofing and

damp proofing

IS:1489 	Indian Standard Specification for portland - pozzolona cement

IS:1566 	Indian Standard Specification for Methods of Sampling and analysis of Concrete

IS:1709 	Code of practice for laying damp proof treatment using bitumen felts

IS:1786 	Indian Standard Specification for cold twisted steel bars for concrete

reinforcement

IS:1791 	Indian Standard Specification for batch type concrete mixers

IS:2185 	Indian Standard Specification for hollow cement concrete blocks

IS:2210 	Indian Standard Specification for design of reinforced concrete shell

structures and folded plates

IS:2386 	Indian Standard Specification for methods of test for aggregates for

concrete  Part I to VIII

IS:2502	Indian Standard code of practice for bending and fixing of bars for

concrete  reinforcement

IS:2505 	Indian Standard Specification for concrete vibrators, immersion type

IS:2506 	Indian Standard Specification for screed board concrete vibrators

IS:2514 	Indian Standard Specification for concrete vibrating tables

IS:2722 	Indian Standard Specification for portable swing weigh batchers for

concrete (Single and Double Bucket Type)

IS:2751 	Code of Practice for welding of mild steel bars used for reinforced

concrete construction

IS:2770 	Indian Standard Specification for method of testing bond on reinforced Concrete

IS:3025 	Indian Standard Specification for methods of sampling and test

(physical and chemical) for water used in industry

IS:3201 	Indian Standard Specification for design and construction of precast

Concrete  trusses

IS:3370 	Indian Standard Specification for code of practice for concrete

structures for  storage of liquids

IS:3550 	Indian Standard Specification for method of test for routine control for

water used in industry

IS:3558 	Code of Practice for use of immersion vibrators for consolidating concrete

IS:3590 	Indian Standard Specification for load bearing light weight concrete blocks

IS:3696 	Safety code for scaffolding and ladders

IS:3812 	Indian Standard Specification for fly ash for use as admixture for concrete

IS:4031 	Indian Standard Specification for method of tests for hydraulic cement

IS:4082 	Indian Standard Specification for recommendation on stacking and

storage of  construction materials at site

IS:4090 	Indian Standard Specification for design of reinforced concrete archs

IS:4634	Indian Standard Specification for method of testing performance of

batch type concrete mixes

IS:4656 	Indian Standard Specification for form vibrators for concrete

IS:4925	Indian Standard Specification for concrete batching and mixing plant

IS:4926	Indian Standard Specification for ready mixed concrete

IS:4990	Indian Standard Specification for plywood for concrete shuttering work

IS:4991 	Indian Standard Specification for blast resistant design of structure for

explosion above Ground

IS:4995	Indian Standard Specification for design of Part I&II concrete bins for

the storage  of granular and powdery materials

IS:4998 	Indian Standard Specification for design of reinforced concrete chimneys

IS:5512 	Indian Standard Specification for flow table for use in tests of hydraulic cement and pozzolanic materials

IS:5513 	Indian Standard Specification for vicat apparatus

IS:5515 	Indian Standard Specification for compaction factor apparatus

IS:5551 	Indian Standard Specification for precast concrete coping blocks

IS:5817 	Indian Standard Specification for method of test for splitting tensile strength of  concrete cylinders

IS:5891 	Indian Standard Specification for hand operated concrete mixers

IS:6452 	Indian Standard Specification for high alumina cement for structural use

IS:6909 	Indian Standard Specification for super sulphated cement

IS:6923 	Indian Standard Specification for method of test for performance of

screed board  concrete vibrators

IS:6925	Indian Standard Specification for method of test for determination of

water  soluble chloride in concrete admixtures

IS:7242 	Indian Standard Specification for concrete spreaders

IS:7246 	Indian Standard Specification for table vibrators for consolidating concrete

IS:7251	Indian Standard Specification for concrete finishers

IS:7320 	Indian Standard Specification for concrete slump test apparatus

IS:7861 	Indian Standard Specification for recommended Part I&II practice for

extreme weather concreting

IS:7969 	Safety code for storage and handling of building materials

IS:8041E 	Indian Standard Specification for rapid hardening portland cement

IS:8112 	Indian Standard Specification for high strength ordinary portland cement

IS:8142 	Indian Standard Specification for determining setting time of concrete

by  penetration resistance

IS:8989 	Safety code for erection of concrete framed structures

IS:9013 	Indian Standard Specification for method of making, curing and determining compressive strength of accelerated cured concrete test  specimens

IS:9077 	Code of practice for corrosion protection of steel rails in RB and RCC

construction

IS:9103 	Indian Standard Specification for admixtures for concrete

IS:9417 	Indian Standard Specification for welding cold worked steel bars for

reinforced concrete construction.

17.0	REINFORCEMENT STEEL:- Reinforcement Steel shall be procured by the contractor only. Reinforcing steel shall be clean and free from loose mill scales, dust, loose rust and coats of paints, oil, grease or other coatings which may impair or reduce bond.

17.1	Mild steel reinforcement shall cover all hot rolled mild steel bars conforming to IS 432 (part-I) Grade-I.

17.2	High yield strength deformed bars reinforcement either hot rolled deformed steel bars conforming to IS-1139 or cold twisted deformed steel bars conforming to IS 1786 shall be used unless otherwise specified. Grade of Reinforcement Steel shall be Fy 500 / Fy 550 grade

17.3	Structural steel sections and plates shall conform IS: 226 and IS : 2062 The quoted rate shall include the cost and conveyance of all materials, labour, tools, tackle, plant and equipment, cutting, bending, placing in position, binding wires etc. complete for finished item of work.

18. 	Plastering

A. Sand for plaster shall have the characteristics specified in IS:1542.

The  sand  shall  not  contain  any  harmful impurities, as  specified in Clause 3.3 of  IS:2117.  The maximum quantities of clay, fine silt, fine dust  and  organic  impurities in sand shall not exceed the following limits.

a . 	Clay, fine silt and fine dust     : 	Not more than three (3) percent

(determined in accordance with      	by weight.

IS:383, Appendix C and also

IS:2386 Part II)

b. 	Organic impurities                : 	Below that indicated by comparison

(determined in accordance with      	with standard solution specified in

IS:2386 Part II)                    		Clause 6.2.2 of IS:2386 Part II.

B.   Plaster shall be applied only when walls are perfectly dry.  Jutting or recessed edges shall  have  sharp  or  suitably  round corners,  as  specified  by the engineer.  Plaster of  all kinds, either smooth or  round  finished,  shall  never  show  cracks,  faulty  alignment,  either  in horizontal or  vertical planes, detachment from walls , blisters or  other faults and  shall  have  a  uniform  and  perfectly  smooth             appearance.   However,  the  new  plaster  shall   not   be  trowelled  to  a  glazed surface since white wash would not adhere to it.

C. Any  faulty  plastering  shall  in any event be removed and replaced at the contractor's expense at the sole discretion of the engineer.

D. The  joints of brick work and masonry shall be raked out to 10 mm deep with mortar still green  to  form  key  for  the cement  plaster  and  surfaces  to  be  plastered,  if  not  sufficiently  rough,  shall  be   thoroughly   picked   and  roughened to  provide  a  good  bond  for the plaster.  The rates for plastering shall be inclusive  of  preparing  the  surface as above.

E. Cement and sand shall be mixed dry  and  then  just  enough  water added  to  form an easily workable paste.  In no case shall mortar which has been  allowed  to  stand  more  than  twenty (20) minutes after mixing, be used.

F. The surface  of  brick  work,  stone,  concrete  and  other structures to be plastered shall be thoroughly cleaned from dust.   dirt,  oil,  salt  and bituminous spots, wetted, as directed before the application of the rendering coat.

G. All scaffolding log  holes  shall  be  properly  filled  in advance of plastering as scaffolding is being taken down.

H. Patches  of  plaster  nearly  150 mm x 150 mm should be put three (3)  meters  apart  horizontally  and  vertically  to correct plane and  to  the specified thickness.  In case of  floors  and  ceilings,  the  mortar  slab  shall  be  truly  horizontal  or  to  specified slope and shall be provided 3  meters apart in both directions.

I. The plaster shall then be laid in single  coat  correct  to  the line connecting the                150 mm x 150 mm patches laid beforehand.   This  shall  be  beaten  with thin strips of bamboo  about one meter long to  ensure  thorough  filling  of  the joints  and  then  brought  to  a true surface by working a wooden straight edge reaching  across  the  patch  as  with  small upward and sideways movement at a time.  The surface                   shall be finished smooth with wooden floats and shall be of first   class   workmanship  of  required  texture  to  the satisfaction of the  engineer.    Excessive  trowelling  or overworking the  float  shall  be  avoided.    During  this                 process a solution of live putty shall be  applied  on  the surface to  make  it  workable.  In case of internal walls,  the plaster shall be left off in a  straight  line  225  mm above the  floor  level.  This together with portion of the floor near  the  wall  shall  be  plastered  together,  the junction  being curved to a radius of 35 mm or larger if so specified on the drawings.

J. For any increase in plaster thickness due to irregularities in brick work face, the contractor will not be entitled for  any extra payment.

K. Proper precautions shall be taken to see that each coat  of plaster  is cured for a   maximum period of fourteen (14) days by an approved method.  Curing shall be done as  soon  as  the applied  plaster  has  hardened  enough  so  as  not  to be  damaged.  The dates on which plastering is  done  shall  be legibly  marked  on  the various sections plastered so that curing for the specified period can therefore be watched.

L. The  contractor shall take every precaution, right from the commencement of plaster work to prevent  any  defects  that  may  appear  on  the  surface of the plasters, and shall be  responsible to make good any portion of the work  which  in  the  opinion  of  the  engineer  required  removal  and/ or  redoing.

M. The uneven face plastering 20 mm thick shall be applied in  two layers. The  first  coat 17 mm thick with the second coat  4  mm  thick  applied  after  the  under   coat   has  sufficiently  set  but  not dried and in any case within 48 hours.  The plaster of under coat when brought  to  a  true surface  with  a wooden straight edge, the surface shall be  left rough and furrowed 2 mm deep with  a  scratching  tool  diagonally both ways to form key for the finishing coat.

N. Plastering  of  the  ceiling  shall  be  done  before  wall   plastering.  Wall plastering shall be done from the ceiling  downwards.

O. In  suspending work at the end of the day the plaster shall be  left,  cut  clean  to  line   both   horizontally   and vertically,  when  recommencing  the plastering the edge of  the old work shall be scrapped, cleaned and  wetted  before plaster  is  applied to adjacent areas to enable the two to properly join together.  Plastering work shall be closed at  the end of the day on the body of wall and not near than 15 cm to any corners or recesses.  Horizontal joints in  plaster work  shall not occur on parapet tops and coping, as these invariably lead to leakage.   No  portion  of  the  surface shall be left-out initially to be patched up later on.

P. If  directed  by  the  engineer,  the  contractor shall use approved  water  proofing  admixtures   made   by   reputed  manufacturer in  the  mortar  for  plastering  work.    The quantity to be used etc., shall be in accordance  with  the manufacturer's instructions subject however to the approval of the  engineer.    These  admixtures  shall  not  contain calcium chloride unless specially allowed by  the  engineer and shall  conform  to  IS:2645.  payment shall be made for actual quantity  of  such  admixtures  used  unless  it  is  already covered in the rates for the work concerned.

Measurement:

Plastering on walls and ceilings shall be measured by their actual   finished  surface,  without  taking  into  account jutting parts, etc., no special allowance  or  extra  price  shall  be  computed  for  these  parts, nor for corners and angles.  Prices are intended either  for  plane  or  curved surfaces.    Provisions  of  transition  grooved  mouldings  between walls and ceiling or between walls, with radius not                   larger than 150 mm is also included in the  price,  keeping  in  mind  that  plaster work shall be measured also in this case as having sharp corners.

All area openings, doors, windows, fan openings etc., shall be deducted while paying for plastering work.  The  plaster prices  are  intended  to  include also finishing at bottom  after completion of floors.

Plastering shall  be  measured  by  their  actual  finished surface in square meters.

18.1	For Walls (Uneven faces):	The walls of uneven faces of superstructure are to be Smooth/ sponge plastered in one coat in 20 mm thick in CM (1:5). The dubara Smooth/ sponge finish plastering is to be done on uneven faces of wall as per the schedule-A and APSS.

18.2	For Walls (Even faces) :	The walls of even faces of superstructure are to be dubara smooth/ sponge plastered in one coat in 12mm thick in CM (1:5). Smooth finish plastering is to be done on even faces of wall as per the schedule-A and APSS.

18.3	Under side roof slab/Ceiling:-	The underside roof slab (i.e. ceiling) is to be finish plastered 12mm thick in one coat in CM(1:3) at all heights. The sponge finish plastering is to be done as per schedule-A and APSS.

18.4	Over RCC Roof Slab:- 	Provided Impervious coat over exposed RCC Roof slab  surfaces to required slopes with Polymer Acrylic Water Proofing layer of  approved make as per manufacturer's specifications and over the layer 25 mm average thickness of screed cement concrete in CC 1:2:4 using 6 mm  coarse aggregate with mixing of integral water proofing chemical at 150 ml  per 50 kg of cement and over the screed concrete 4mm thick  neat coat of cement plaster in CM 1:4 with mixing of integral water  proofing chemical of approved make at 150 ml per 50 kg of cement and  thread lining of regular intervals of 45 x 45 cm including and cost and  conveyance of all materials, water, all labour charges, chemicals, curing for  specified number of days, rounding off junctions of wall and slab, all leads, lifts, heights, levels and floors etc. complete as directed by the engineer-in-  charge for finished item of work.

18.5	For Drains:-	The walls of drains, UG sump, O.H. tank, columns in cellar floor,   parapet walls  are to be plastered with CM(1:5) 12 mm thick for drains at all heights. The plastering is to be done as per schedule-A and APSS.

18.6	For Compound wall:-	The retaining wall are to be plastered with CM(1:5) 20 mm thick for all heights. The plastering is to be done as per schedule-A and APSS.

18.7	For Sunken Portions:- Providing and laying of Impervious coat in Sunken portion of slabs to required slopes with CM 1:3 of 20 mm thick per-mixed with water proofing chemical compound of approved quality & make and ISI Mark at 1 kg per one bag of cement (or as per the recommendations of the manufacturers) laid over sunken / roof slab when it is green, rendered smooth with a floating coat of neat cement  including and cost and conveyance of all materials, water, all labour charges, chemicals, curing for specified number of days, rounding off junctions of wall and slab, all leads, lifts, heights, levels and floors etc. complete for finished item of work and as directed by the engineer-in-charge.

18.8	The quoted rate for plastering works shall include

  - Erecting, dismantling and removing of the scaffolding.

  - Preparing the surface to receive the plaster.

  - Providing cement plaster with specified finish and specified thickness.

  - All labour, cost and conveyance of all materials, use of tools and equipment to complete the plastering as per specification.

  - Curing for 14 days.

  - Any grooves, bands etc, if shown on the drawings or as directed by the Engineer-in-charge.

  - All lifts and leads.

  - All wooden frames, steel frames or other fixtures which are required to be painted or polished subsequently shall be cleaned after the plastering work is complete for finished item of work.

19.0     FLOORING:-

- Flooring with a bed of 100 mm thick in CC (1:4:8) using 40 mm and 20 mm size HBG metal 50% each.

- Flooring with Vitrified Tiles of 1st Class Quality 8mm thick of 600x600x8 mm size for floorings of Rooms, passages set over CM 1:3 of 12 mm thick and neat joining with white cement including cutting , laying,  over CC bed already laid including neat cement slurry of honey like consistency, spread at the rate of 3.3 kg of cement per m², jointed to full depth, (Joints must be flushed )  with white cement  paste mixed with pigment when required including cost and conveyance of cement and all materials, labour charges, at all levels, heights and floors, curing all incidental charges etc. complete as directed by the engineer-in-charge and for finished item of work ..

- Flooring with Ceramic  Tiles of 1st Class Quality 7.3 mm thick of 300x300x7.3 mm size  of approved brand , shade and design of different sizes laid over a floor bed of  CM 1:3 of 12 mm thick base coat  and neat grey cement slurry of honey like consistency spread at the rate of 3.3 kg of cement per m² and pointed to full depth, (Joints must be flushed )  with white cement  paste mixed with pigment when required including cost and conveyance of cement and all materials, labour charges, at all levels, heights and floors, curing etc

- Flooring with Adanga green Marble Stone of good quality 20 mm thick of size for steps  in single piece of 1.5 m for staircase raise and tread and max available length and width piece for staircase lobby laid over CM 1:3 of 12 mm thick and neat joining with white cement including cutting , laying, minimum of five coats of tinoxide  polishing over CC bed already laid including neat cement slurry of honey like consistency, spread at the rate of 1.5 kg of cement per m², jointed to full depth, (Joints must be flushed ) including cost and conveyance of all materials, labour charges, at all levels, heights and floors, curing etc. complete a for finished item of work and as directed by the engineer-in-charge.

- Providing Flooring  in Stilt floor with Parking Tiles ( Pavement Tiles) Tiles of 1st Class Quality of approved colour and pattern 10 mm thick of 300 x 300 mm size set over CM 1:3 of 12 mm thick and neat joining with white cement including cutting , laying,  over CC bed already laid including neat cement slurry of honey like consistency, spread at the rate of 1.5 kg of cement per m², jointed to full depth, (Joints must be flushed )  with white cement  paste mixed with pigment when required including cost and conveyance of cement and all materials, labour charges, at all levels, heights and floors, curing etc. complete as directed by the engineer-in-charge and for finished item of work .

- Skirting/ Dadoing to Walls Bath Rooms and stair case walls with Decorated back ground glazed Tiles of 1st Class Quality 7.3 mm thick of 200 x 300 mm size set over CM 1:2 of 12 mm thick and neat joining with white cement including, cutting, laying cement slurry of honey like consistency spread at the  rate of 3.3 kg/m² and filling the joints with white cement paste mixed with pigment of matching shade is to be done including cost and conveyance charges of cement  and  all other materials to site, seigniorage charges, incidental and operational charges, all labour charges for mixing mortar, finishing,  all leads and lifts, including cost and conveyance of all materials, labour charges, at all levels, heights and floors, curing all incidental charges etc. complete for finished item of work and as directed by the engineer-in-charge.

- Providing Dadoing to Walls  faces of Lifts, with Chilly Red or any other approved colour of Polished Granite Stone of thickness 15 mm laid over base coat of CM (1:2) of 12 mm thick applying araldite to the stone and pointing with 6 mm  bewel edged grooves matching colour cement set over with neat cement slurry of honey like consistency spread at the rate of 3.3 kg/m² and filling the joints with white cement paste mixed with pigment of matching shade including cost and conveyance of all materials, labour charges at all leads, lifts, floors, levels and heights, all incidental charges  etc. complete for finished item of work and as per the approved drawings and directions of the engineer-in-charge.

20.	DOORS, WINDOWS & WOODEN PARTITIONS :

20.1	Supply and fixing doors with the frame of the door shall be made of well seasoned MT wood of cross section 125x75 mm. The shutter shall be made of ISI marks flushed door with decolam sheets pasted on both sides with Teak beading 40 mm width all-round. Frame shall be painted with two coats of synthetic enamel paint of approved colour over one coat of primer over luppum with spray  with 3 no 150 mm Aluminum hinges , 1 no Aluminum door stopper 150mm, 2 no 300 mm Aluminum aldrops, 2 no 300 mm Aluminum tower bolts, 2 no 150 mm Aluminum fancy door handles. The quoted rate shall include cost and conveyance of the materials, fixing, labour charges, tools, handles, locking arrangements, and other fixtures & fittings for finished item of work as directed by the Engineer-in-charge.

20.2    Supply and fixing of aluminum anodized sliding windows & ventilators as per drawings with all required accessories such as stoppers, bolts, weather stripping etc., for all sizes and sections in accordance with approved drawings & as per IS 1948-1961 with top & side frames of size 62.63X36X1.5 mm thick and bottom frame of size 62.6X31.6X1.5 mm thick sloping outwards for drainage & fixed, sliding shutter with 40X27.5X18 X1.5 mm interlocking section 40X18X1.5 mm size for top side & bottom sections interlocked for weather scaling & mounted on Nylon rollers of lift type with 5mm thick plain glass glazing, fitted with Aluminum glazing clips & suitable rubber beeding for all sizes of windows( Aluminum sections shall be of standard make as approved by Engineer in Charge.

20.3    Supply and fixing of Structural glazing made of pre painted steel (base ;steel as per IS 513 of 0.6 mm thick D quality, galvanized  as per IS 277 with Zinc of 120 GSM ) Primer coated with epoxy primer  of 5-7 microns thick, finish painted with a polyester paint of 12-16 microns thick and back coated with 5-7 microns thick alkyad  backer. section for outer frame should be 46x52mm, beading should be 18X25mm .  the glazing should be paneled with 5mm thick plain float glass with ethylene propylene diene monomer (EPDM) gaskets.  the sections are tobe cut to length, mitre joined with corner bracket.  Center mullions are to be fixed suing mullion  cap.  Handle made of high grade Aluminum powder coated and nylon receiver. Gaskets made of ethylene propylene diene monomer (EPDM) corner brackets made of CRCA with zinc phosphate. Mullion caps made of glass filled nylon. The above frames should be fixed to the concrete- masonry walls be means of self expanding screws. Including all taxes and complete for finished item of work. (Fixed glazing2'-0"X3'-0" (609.6 X914.4mm) grid outer frame section size of 46x52 mm)  S.No.694 in SSR and as directed by Eng-in -charge.

20.4	Wooden Partition:

20.4.1	Supply & Fixing of wooden partitions with double skin 8mm thick plywood on both sides with supporting frame of 3"X1.5" section of 1'6"X1'6" grid, 1.5mm thick decolam pasted on both sides, 6mm thick glass for openings with necessary beeding including labour charges fixtures with necessary labour & hardware etc., for complete item of work

20.4.2	Supply & Fixing of flush door of 30mm thick with laminate finish on both sides, 6mm thick glass for glazed portion including labour charges fixtures such as hinges, cylindrical lock & hardware etc., for complete item of work

21.        PAINTING  IRON WORK :

Paint to be used for various items of work shall be of best quality and shall be obtained ready mixed in sealed containers from approved manufacturer.  The Contractor shall obtain the Engineer's approval for the make and colour of the paint he proposes to use.  If required, polish for woodwork shall be tested as per IS:5807 (Parts I & III).

All surfaces shall be thoroughly cleaned of all dirt, loose particles and rust and approved prior to application of paint.  For Steel gates & Rolling shutter surfaces, a priming coat without colouring matter shall be first applied after which all holes, cracks, etc., shall be stopped with putty and all knots properly killed with quick lime.  Workmanship shall conform to IS:1477 (Parts I &II and 2338 (Part I).

Specified number of coats shall be applied and at least 24 house shall elapse between the application of successive coats.  No painting shall be carried out on exterior work in wet weather or on surfaces which are not entirely dry.

Painting rate shall include all necessary scaffolding, cradles and plant.  Measurements will be on the basis of Sq.m. for doors and windows, only the projected area will be measured, if such painting is not already a part of the item, without deducting for the glazed portions though not painted.  The Contractor's rate should take this into account.

22        GATES and ROLLING SHUTTERS:-

22.1	Supply and fixing of Iron gates as per approved drawing with approved thick two coat of enamel over coat of anti rust paint including cost and conveyance of all materials and labour charges  for fabrication and fixing, painting, hold fasts, hinges, locking arrangements etc. complete  as directed by Engineer-in-charge SNO:144 IN SSR as directed by Eng-in- charge. Mode of Payment : The payment for the windows and ventilators shall be made on the basis of area in m² specified.

  - Supply and fixing of Collapsible steel shutters with verticle, double channel of 20x10x2mm of 100mm center Bracers with flat iron 40x40x6 mm with 38 mm dia steel pully with all fixtures and furniture as per spl.spn.1105  including cost and conveyace of all materials and labour charges etc. complete and as directed by Engineer-in-charge S.NO.116 IN SSR as per directions of Eng-in-charge.

23	RCC   DROP WALLS :

Sun breakers and drop walls at all elevations are to be provided in CM (1:2) 50 mm thick over rabbit wire mesh & 6mm dia. Reinforcement steel. The rate shall be inclusive of reinforcement steel (6 mm @ 150 mm C/C both ways), cement, all labour ,leads, lifts chicken wire mesh, shuttering, scaffolding cost of cement mortar and finishing with ordinary plastering for finished item of work as directed by Engineer-in-charge.

24      PAINTING :

24.1	OUTSIDE WALLS :

Painting to External Faces of walls(outside) in all floors as specified with two coats of ACE or equivalent quality paint of approved colour make and shade over one coat of white cement primer including cost and conveyance of all materials, labour charges at all leads, lifts, heights, levels and floors, all incidental charges etc. complete   for finished item of work.

24.2	INSIDE WALLS :

Painting  in all floors as specified with two coats of oil bond distemper  of approved colour make and shade over one coat of white primer including cost and conveyance of all materials, labour charges at all leads, lifts, heights, levels and floors, all incidental charges etc. complete   for finished item of work .

The  rate quoted includes cost of all materials, conveyance, taxes, scaffolding, all leads, lifts, all heights, levels, floors, curing ,all incidental charges etc. complete and as directed by Eng-in-charge.

1. 	No painting work shall be started unless specimen colours and shade are submitted in advance to the  Executive Engineer/ Civil/ Gr.Hyderbad for approval, such approval of paint specimen by the Engineer does not relieve the contractor of his full and entire liability as to the life and quality of paint.

2. 	The Engineer-in-charge while work is in progress, may take samples of the products employed in the different Operations in order to have them analyzed and tested as deem fit at the contractor’s expense.

3. 	Any deviations and defects shall have to be rectified by the contractor at his own expense. Contractor shall protect the work and materials by suitable covering or other method acceptable to Engineer-in-charge.

4. 	The contractor shall remove all the paint and varnish spots from floors, walls, glass panels and other surfaces and restore them to original condition. No impression of brushes should be visible on the wall surface.

5.   	Painting of second coat over the first coat should be right angle to the first coat application direction

Supply & Application of One Coat of Altek Water Based Cement Primer & Two Coats of Altek Alltimate (100% Pure Acrylic Emulsion Paint) after making surface even and free from all dents including cost and conveyance of all materials, labour charges at all leads, lifts, heights, levels and floors, all incidental charges etc. complete   for finished item of work .

24.3	Providing Two coats of Painting to New Wood Works ie. doors in wooden frames and flush shutters, in synthetic enamel paint of approved make, colour and shade over single coat primer coat of wood primer, including cost and conveyance of all materials, labour charges, cost of brushes, emery papers, applying putty wherever necessary to get new finish etc complete, for finished item of work and to the satisfaction of engineer-in-charge.

24.4	PREPARATION OF SURFACE : The surface is to be prepared as per the relevant clauses of APSS/ISS and as directed by Engineer-in-charge. Application of primer and number of coats to be applied shall be as specified and as directed by Engineer-in-charge and as per manufacturer’s specification. The surface on finishing shall be absolutely uniform and smooth.

24.5	The Quoted rate shall include the following.

  - Supplying the paints of approved shade and make..

  - Preparing different surfaces to be painted as per standard specification.

  - Providing and erecting scaffolding and removing the same wherever necessary. Safety measures are to be followed to avoid mishaps. at the work site

  - Lifting the materials to all heights.

  - Application of Paint as per standard specification.

  - Curing and protecting the painted surface.

  - Labour Charges, slandered tools and tackles should be used on the work like brushes etc.

  - Any other incidental charges etc complete for finished item of work.

25	PAINTING NEW STEEL WORK :

  - New Steel work is to be painted with approved synthetic enamel paint (Asian/ Berger or equivalent) in two coats over one coat of wood primer.

  - The Steel surfaces to be painted must be thoroughly dry, clean and smooth and must be approved by the Engineer-in-charge before any paint is applied.

  - Primary Coat: It shall be of approved brand and shall be brushed uniformly free from brush marks etc.

  - Stopping: After priming all small holes, cracks, open joints and similar minor defects of every kind shall be stopped with approved brand readymade putty.

e)  Synthetic enamel paint:

    - PAINT: Synthetic enamel paint and primer of approved brand, manufacturer and shade shall   be used.

    - PREPARATION OF SURFACE: Preparation of Surface shall be as per standard specification of APSS. The primary and number of coats to be applied shall be as specified and shall be applied as per manufacturer’s specification.

    - Ready mix paint only preferred. No admixtures are allowed to add to the paint.

26	C.I. COVERS

Providing and Fixing of Heavy duty C.I. Covers confirming to IS:12592 (Part1&2) of double seal type including Frames and locking arrangement over the Under Ground Sump and Over Head Tank of size 600 x 600 mm and suitable thick and weight not less than 38 kg inclusive of cover and frame in the RCC Slab of tanks, including cost and conveyance of all materials, labour charges etc complete for finished item of work

27	RCC HUME PIPES

Supplying, laying and Jointing RCC Hume Pipes of S & S ends of 250 mm dia. of NP2 Class including cost and conveyance of all materials,   labour charges, leads and lifts and  finishing with ordinary plastering for finished item of work.

28.	PLUMBING & SANITARY ITEMS:

  - SALT GLAZED STONE WARE PIPES:

Stone ware pipes shall be salt glazed and free from cracks, deformities and imperfections. They shall be cylindrical straight and to standard dimensions. They shall be made of hard burnt stoneware of dark grey colour and thoroughly glazed and shall give sharp clear sound when struck with a light hammer. The pipes shall conform to the requirements of IS:651 and shall be of perfect potteries of approved equivalent make.

  - CAST IRON PIPES:

Cast iron pipes, where called for on the drawings shall be good tough quality dark grey on fracture and capable of being worked with a driller file. Cost iron pipes and fittings shall be sound with smooth inner and outer surface, free from laps, pin holes and other imperfections and shall ring clearly when struck all over with a light hard hammer. Cast iron pipes supplied by the manufacturer shall bear coating of bitumen by hot dipping, which should neither flow at 77 °C temperature nor brittle at 0 °C temperature or chip off when lightly scribed with a pen knife. The coating shall be smooth and tenacious. Pipes and fittings for drainage (Soil, Waste, and vents) shall conform to IS:3989 and/ or IS: 1729 and as specified.

All cast iron pipes and fittings shall be of Indian Iron & Steel Company, manufacture or other approved equivalent.

  - GALVANISED IRON PIPES:

Galvanized Iron pipes and fittings where called for on the drawings shall be of galvanized mild steel or galvanized wrought iron. The pipes shall be ‘B’ class manufactured by Indian Tube Company or Bharat Steel Tubes or TATA or other approved as called for. The fittings shall be “R” brand fittings of Mehta Corporation (Ahmedabad) or approved equivalent as called for. All pipes and fittings conform to IS:1239 – Part-I, Part-II and the galvanizing shall conform to IS:4736. On delivery to site, the pipes and fittings shall be inspected for the galvanized coating. Pipes with damaged coatings shall be immediately segregated.

  - PVC PIPES:

PVC pipes where called for shall be either un-plasticized PVC pipes or High density polyethylene pipes supplied with appropriate fittings. The pipes and fittings shall be 6.0 kg/m² pressure class for sewer pipes ie 110mm and 90 mm  pipes (PVC/SWR) an 4.0 kg/cm² pressure class for waste water pipes. Plastic Pipes shall be handled with care and stacked in a place protected from the sun. All plastic pipes and fittings shall be manufactured by SUDAKAR or NOCIL or WAVIN or NANDI or approved plastic pipes and fittings shall conform to Indian Standard IS:4984 or IS:4985.

  - WATER SUPPLY FITTINGS:

All water supply fittings (including supplying, fitting and accessories) shall be of brass/copper, heavy chromium of approved make and design specified. The fittings shall be cast fittings of screw type, machined and threaded properly for fixing to the supply pipes. The plating shall conform to IS:4827. The fittings shall be supplied complete with chromium plated matching flanges nuts and extension pieces if required lengths. Metallic washers where required shall also be of chromium plated brass. All bib cocks and stop cocks shall conform to IS:781, Pillar cocks shall conform to IS: 1795. Bath fittings to IS:1701, Bath filler, shower arm, rose, sockets and other fittings shall match the supply fittings in construction and appearance. All fixing accessories and screws shall be similar fittings. All fixing, all washers shall conform to IS:4326.

  - SANITARY FIXTURES:

All glazed vitreous shine sanitary ware fixtures shall be of best Indian made of approved manufacture conforming to IS:2556. These shall be non-porous and fully vitreous, with all the visible portions perfectly glazed should be absolutely free from hair line cracks, pin holes and local depressions. These shall have perfectly symmetrical uniform and smooth curves.

  - WASTE FITTINGS:

All waste fittings (waste, chain, pop up, overflow, spreaders caps etc.) shall be of brass/copper heavy chromium plated of approved make and designs specified and match the supply fittings. They shall conform to IS: 2963.

  - VALVES:

All valves (gates, globe, check, safety etc.) shall be either all brass or gun metal valves suitable for the particular service. All valves shall be for the particular duty and designs called for similar to ‘leader’ or G. G. Bombay make or approved equivalent, valves shall be tested to 21 kg/cm² pressure at manufacturer’s works.

Valves shall either be of the screw type or flange type, with suitable flanges and non-corrosive bolts and gaskets. Tail pieces as required shall be supplied along with valve gate, globe and gate, globe and check valves shall conform to IS:778 and non-return valves to swing check type reflux (non return valves IS:5312 part-1).

BALL VALVES WITH FLOATS: Ball valves with floats to be fixed in storage tanks shall consists of cast brass lever arms having copper balls (28 SWG) screwed to the arm integrally. The copper ball shall have bronze welded seams. The closing /opening mechanism incorporating the piston and cylinder shall be of a non-corrosive metal and include washers. The size and construction of ball valve and float shall be suitable for desired working pressure operating the supply system. Ball valve shall be supplied with brass hexagonal back nuts to secure then to the tanks and socket to connect to supply pipe. All brass valves with floats shall conform to IS:1703.

  - FLOOR TRAPS and NAHANI TRAPS:

Floor traps, Nahani traps and urinal traps shall be provided wherever necessary and shall be of cast iron of size required, of approved design incorporating a deep seal size required (6cm. minimum) and venting device unless otherwise indicated. The traps shall be supplied with a specially cast iron extension piece with required number of sockets in appropriate directions to receive the waste/soil pipes from wash basin/bath tub/urinals.

28.10 PIPE HANGERS, BRACKETS ETC:

Sturdy hangers, brackets and saddles of approved design shall be installed to support all pipe lengths which are not embedded over their entire run. The hangers and brackets shall be fabricated from suitable M.S Rolled sections. The hangers and brackets shall be adjustable heights and painted with red oxide primer, clamps, collars and saddles to hold pipes shall be provided with suitable gaskets. The Brackets and hangers shall be designed to carry the weight of pipes safely.

All pipes and shall be secured near every joint and halfway through every pipe length unless otherwise specified.

28.11GRATING FOR FLOOR TRAPS:

Gratings made of 3 mm thick brass heavily chromium plated shall be installed to cover all floor traps and floor drains. The gratings shall be of size required and be square or circular in shape as called for. The gratings shall be supplied complete with matching chromium plated Brass screws, and brass rings to fasten the gratings to the floor on traps.

28.12 COWLS:

Cowls of cast iron of proper size shall be supplied to cover all open terminals of soil, waste, vent. The cowls shall be of the indicated design vent away type, bituministic coated and provided with a tail piece to fit snugly in the receiving pipe.

28.13 ALIGNMENT AND EXCAVATION OF TRENCHES:

28.13.1 ALIGNMENT AND GRADE: - All pipes shall be laid true to alignment and gradients as shown on the drawings. No deviations from the lines, depths of cuttings or gradients called for on the drawings shall be permitted without the approval in writing by the Engineer-in -charge.

    - SETTING OUT TRENCHES:- The contractor shall set out all trenches, man holes and such other works to true and alignment as called for. He shall provide the necessary instruments for setting out and verification of the same. All trenches shall be laid to true grade and in straight lines and as shown on the drawings. The trenches shall be laid to proper levels by the assistance of rods and sight rails which shall be fixed at intervals not exceeding 10 meters or as directed.

    - EXCAVATION OF TRENCHES FOR PIPES:- The trenches for pipes shall be excavated with bottom formed to levels and gradients as shown on the drawings or as directed. In soft and filled in Ground the contractor may require the trenches to be excavated to a greater depth than that shown on the drawings and to fill up such excavation with concrete consolidates to bring the excavation to the required levels as shown on the drawings. All excavation shall be properly protected where necessary by suitable trimmings approved.

Excavation below water table shall be done after dewatering of the trenches. No blasting shall be allowed without prior approval in writing from the Engineer in-charge. It shall be carried out under thorough and competent supervision, with written permission of the Engineer in-charge taking full precautions connected with blasting operations. All excavated earth shall be kept sufficiently clear of the trenches.

All pipes, water mains, cables etc., met in the course of excavation shall be carefully protected and supported. Care shall be taken not to disturb the cables, the removal of which shall be arranged by the owner.

    - BACK FILLING:- Refilling of the trenches shall not be commenced until the length of the pipe there in has been tested and approved. Where the pipes are unprotected by concrete hunching selected fine material shall be carefully hand packed around the lower half of the pipes so as to buttress them to the sides of the trench. The refilling shall then be continued in 150 mm thick layers over the top of the pipes using selected fine hand packed material, watered and rammed on both sides of the pipes with a wooden rammer. The process of filling and tamping shall proceed evenly in layers not exceeding 150mm in thickness. Each layer being watered and consolidated so as to maintain an equal pressure on both sides of the pipe line. In gardens and fields, the top soil and turf if any shall be carefully replaced.

  - RILLING & CUTTING:-

Drilling and cutting of installed pipe work and masonry shall be restricted to absolute minimum. Where such cutting and drilling is unavoidable it shall be executed only with prior permission. All cutting and drilling shall be pre-determined and suitable sockets and specials shall be employed to effect necessary connections. All cutting and drilling shall be executed by skilled workmen with proper tools. The disturbed surfaces shall be restored to the satisfaction of the Engineer at site.

  - LAYING OF PIPES AND JOINTING OF PIPES:

    - General: The pipes shall generally be laid with sockets leading uphill and shall rest on solid and even foundations for the full length of the barrel. To accommodate sockets depressions shall be formal in the foundations sufficiently deep to allow ample space of the pipe jointer to work right round the pipes. Each separate pipe shall be individually set for line and levels. Pipes shall always be installed in accessible positions. Except where absolutely necessary and indicated the pipes shall be installed in wall chase/floor.

    - Salt Glazed Stoneware Pipes: The laying and jointing of stoneware pipes shall be executed in accordance with Code of Practice for laying of glazed stoneware pipes as per IS:4127. Salt glazed stoneware pipes shall be jointed as follows:

Hemp shall first be wrapped round the spigot of each pipe and spigot shall then be placed into the socket of the pipe previously laid. The pipe shall then be adjusted and fixed in the correct position and the hemp caulked tightly home as not to fill more than quarter of the total depth of the socket. The remainder of the socket shall then be filled with a stiff mixture of cement mortar (1:1) one part of cement to one part of washed coarsed sand. When the socket is filled shall be formed found the joint with a trowel making an angle of 45 deg. with the barrel of the pipe. After the joint is made, any extraneous material shall be removed from the inside of the joint with suitable scraper. The newly made joint shall be protected until set, from sun, drying winds, rain or dust. The joint shall be cured by keeping it continuously damp for four days.

The inside of the pipes shall be left absolutely clear in bore and free from cement mortar or any other obstruction. These joints shall be tested to ahead of 100 cm for two hours without developing leaks or fall in pressure. In case of leaks, the piping shall be redone in such position and the test repeated till satisfactory result.

    - CAST IRON PIPES:- Cast iron pipes shall be laid and jointed in confirmation with the code of practice for laying of cast iron pipes IS:3114. Cast iron shall be joined by best quality caulking lead free from all impurities. In wet trenches, joints shall be made with lead wood. The spigot shall be centered in the adjoining socket by tightly caulking in sufficient turns for tarred gasket to leave the unfilled required depth of socket for load. Where the gasket has been caulked tightly home a jointing ring shall be placed round the barrel and against the face of the socket. Molten lead shall then be poured into fill the remainder of the socket in one operation. The lead shall then be poured into fill the remainder of the socket in one METRO ZONE.

The lead shall then be solidly caulked with suitable tools by hammering right round the joint to make up for the shrinkage of the molten metal on cooling and shall preferably finish 3mm behind the socket face. caulk

The joints and pipes laid for water supply system shall be tested to pressure of 12 kg/cm² for two hours without developing leaks/fall in pressures. The drainage pipe lines and joints shall be tested to a head of 150 cm for two hours without developing leaks/fall in pressures. In case of leaks, the piping shall be redone in such portions and the test repeated till achieving satisfactory results.

    - GALVANISED STEEL PIPES:- Galvanized steel pipes shall be jointed with screwed and socket joints using screwed fittings. Care shall be taken to remove any burr from the ends of the pipes after threads cutting. White lead or an equivalent jointing compound of proprietary make shall be used, according to the strands of red lead shall not be used fine yarn while tightening. Compounds containing of water, read lead shall not be used because of the danger of contamination of water. Any threads exposed after jointing shall be painted with bituminous paint to prevent corrosion.

Pipes and joints laid for water supply system shall be tested to a pressure of 7 kg/cm² for two hours without developing leaks/fall in pressure. In case of leaks, the piping shall be redone in such portions and the test repeated till achieving satisfactory result.

    - VALVES:-Valves shall be provided at accessible locations on every branch from main lines. In case of valves with screwed female inlet/outlet, each valve shall be provided with a union, on either side and installed in piping system. On external lines, valves shall be installed in brick masonry chambers with a frame and cover as directed by the Engineer-in-charge.

    - PIPING SYSTEMS INSTALLATION, INSPECTION & TESTING:

The soil pipes shall be of minimum diameter of 100 mm and waste pipes of 80 mm. Pipes shall be fixed by means of clamps in two sections, bolted together, built in to the walls, wedged and neatly painted as directed and approved by the Engineer keeping 50 mm distance from the walls. Where indicated, the soil and waste pipes shall be continued upwards without any change/distinction in its diameter, without any bend or angle to the height shown in the drawings.

Unless specified otherwise soil and waste pipes from urinal/wash basin/sinks upto the floor trap shall be of GI medium class pipes (Class B) . All the traps of water closets and urinal traps shall be provided with anti-siphon /relief vent pipes as directed by the Engineer. All terminal manholes shall be provided with vent pipes. This may be dispensed if the upper floor soil stacks connecting to such manholes are vented. All soil, waste and vent pipes shall be given two coats of approved paint.

All connections, between soil, waste and ventilating pipes, and branch pipes shall be made by using pipe fittings with inspection doors for cleaning. The doors shall be provided with 3 mm thick rubber insertion packing and when closed and bolted shall be air and water tight.

Where soil, waste and ventilating pipes are accommodated in shafts, ducts adequate

access to cleaning shall be provided

- SANITORY FIXTURES & FITTINGS:-

  - INSTALLATION OF FIXTURES & FITTINGS:-

The sanitary fittings shall be installed at the correct assigned positions as shown on the drawings and as directed by the Engineer/architect, and shall fully meet with the aesthetic and symmetrical requirements. Fixtures shall be installed by skilled workmen with appropriate tools according to the best practice in the trade. Manufacturers’ instructions shall be followed for the installation of the fixtures. Fixtures in all toilets shall be standard height mounted rigid plumb and true to alignment. The outlets of water closet pans and similar appliances shall be examined to ensure that outlet ends are abutting properly on the receiving pipes before making the joints.

It shall be ensured that the receiving pipes are clear of obstruction. When fixtures are being mounted, attention shall be paid to the possibility of movement and settlement by other causes. A check shall be made to ensure that necessary anchoring devices have been provided for supporting water closets, lavatory basins, sinks, flushing cisterns and other appliances. Where the built-in type of brackets are used, they shall be securely fixed to the slabs and walls by approved means. It shall be ensured that while fixing the fixtures and fittings no tool marks or scratches are developed.

  - PROTECTION OF FIXTURES:- Care shall be taken at all times, particularly after fixing, to protect fixtures from damage. All orifices shall be temporarily plugged during progress of work to prevent obstruction. Fixtures shall be finally cleaned to the satisfaction of the Engineer-in-charge.

  - MISCELLANEOUS WORKS:-

  - CONNECTION TO WATER TANKS AT TERRACE: - The contractor shall provide all inlets, outlets, washouts, vents, ball cocks, overflow, control valves and all such other piping connections including level indicator to water storage tanks as called for. The pipe shall be embedded with puddle flanges as necessary at no extra cost. Suitable float controls of an approved make, securely fixed to the tank and set in a position that water inlet in-to the tank is cut off when filled up to the full water line. The water level in the tank shall be adjusted to 25mm. below the line of the overflow pipe.

Full way gate valves of approved make shall be provided as near the tank except the overflow pipe. The overflow pipe shall be so placed as to allow the discharge of water being readily seen. The overflow pipe shall be as indicated. A stop valve shall also be provided on the inlet water connection to the tank. The outlet pipes shall be fixed above the bottom of the tank as indicated. A wash out pipe shall be provided at the bottom of the tank towards which the flux of the tank is slopping to enable the tank to be emptied for cleaning.

  - DISINFECTION OF PIPES SYSTEM AND STORAGE TANK: Before commissioning the water supply system, the Contractor shall arrange to disinfect the entire system. The filtered water storage tanks and pipes shall first be filled with water and thoroughly flushed out. The storage tanks shall then be filled with water again the disinfecting chemical containing chlorine added gradually while tanks are being filled to ensure thorough mixing. Sufficient chemical shall be used to give the water a dose of 50 parts of chlorine to one million parts of water. If ordinary bleaching powder is used, the proportions will be 150 g of powder to 1000 litres of water. The powder shall be mixed with water to creamy consistency before being added the water in storage tank. If a proprietary brand of chemical is used the proportion shall be as specified by the makers. When the storage tank is full, the supply shall be stopped and all the taps on the distribution pipes opened successively working progressively away from storage tank. Each tap shall be closed when the water discharge begins to smell of chlorine. The storage shall then be filled up with water from supply pipe and added with more disinfecting chemical in the recommended proportions. The storage tank and pipe shall then remain charged at least for three hours. Finally, the tank and pipes shall be thoroughly flushed out before any water is used for domestic purposes.

  - SANITARY APPLIANCES:

The contractor shall furnish all labour, materials and equipment required for supply and installation of various sanitary appliances required for the civil works mentioned in sub-section and as per drawing and specifications.

- WASH BASINS: Wash basins shall be of colour vitreous china of standard size (23” X 20”) 585 x 500 mm. with flat back. Wash basin shall be one piece construction including a combined overflow and soap holder. Wash basins with approved quality chromium plated pillar taps(15 mm.) dia. along with stop cocks, brackets, waste coupling etc., shall be provided. The wash basins shall in all respects conform to IS:2556(part IV).

Wash basins shall be provided with waste couplings, 75 mm. CP Nahani floor trap and connecting pipes.

Mode of Payment: - Rate per 1 No

- INDIAN TYPE OF WATER CLOSET : - The installation shall consist of squatting pan of a specified size 23”(581 mm size ) and make with an integral flushing rim coupled to a ‘P’ or ‘S’ trap with or without an inspection vent as specified by the  Executive Engineer/ Civil/ Gr.Hyderbad . The installation shall be securely fixed level in brick jelly concrete with cement mortar , so that the floor of the privy gently slopes towards the rim of the squatting pan. The outlet of the trap shall unless otherwise specified be connected to the PVC/SWR soil pipe throughout a short length of lead pipe of the same bore by means of a brass socket and a ferrule. The joint between the trap outlet and the brass socket shall be made by cement mortar(1:1) with a packing of yarn. The joint between the PVC/SWR. soil pipe and the brass socket shall be made by caulked pig lead with a packing of yarn.

30 MAN HOLE AND GULLEY TRAPES:-

Man Holes / Inspection chambers with  brick masonry 1.5 m outer dia at bottom and 1 m outer dia at top varying from 1.5 m to 1.0 m including laying of 150 mm CC bed in CM(1:4:8) using 40 mm HBG metal and 0.23 m thick brick masonry walls in CM(1:6) tapering; forming necessary channels and bedding up to the bottom of channels and plastering with CM(1:3) 12mm thick both inside and outside, supply and fixing of heavy duty (20 kg) man hole cover of 508 mm dia   with frame and CI rungs including painting to cover, frame and rungs, cost and conveyance of all materials labour charges, leads and lifts, curing, etc., complete for finished item of work

Gully Trap (150X100 mm) of 1st class, with CI grating and constructing single brick masonry wall chamber of 20"x14"x12" in CM 1:6 over a CC bed 1:5:10 of 100 mm thick and plastering in CM 1:3 for 12 mm thick with 12"x9" CI frame and hinged cover of approved quality including cost an conveyance of all materials to site, labour charges, etc. all complete.

GENERAL TECHNICAL SPECIFICATIONS FOR ELECTRICAL WORKS

1.0 BUSDUCT AT TRANSFORMER SECONDARY:

Bus duct shall be fabricated out of 14 SWG powder coated sheet steel. The bus duct intended for connection between the secondary of 1000 kVA transformer and the incoming feeder of the 415 volts Main Distribution Board shall be dimensioned perfectly to match the transformer / switch board end flanges.

The bus duct shall have ventilation louvers at every 1000 mm intervals on both sides of the duct. Necessary interchange in connections shall be done to maintain the phase sequence. Bus bar supports shall be of SMC.

A copper earth bus of size 30 x 6 mm shall be run throughout the length of the bus duct.

Flexibles of adequate sizes shall be provided at' both transformer and distribution board ends.

2.0    415 volts MAIN / SUB DISTRIBUTION BOARDS

2.1    CONSTRUCTION

i)     	Sheet steel - 2 mm thick for frames and equipment mounting plates 1.6 mm thick for partitions.

ii)   Welded construction - with transport sections bolted together. All such joints are to be           gasketed.

iii)      The cubicles shall be totally dust and vermin proof conforming to IP-54.

iv)	All doors should be of hinged type except bus bar chamber covers which shall be of bolted type. The panels shall he of flush front design, suitable for access from front and rear, except where the boards are mounted against the wall in which case the boards shall be designed for maintenance with front access only. All switch boards enclosures shall be powder coated of approved shade.

v)	The construction shall be such as to facilitate easy extension at both ends. SMC supports and heat shrinkable PVC sleeves shall be provided for bus bars.

vi)	The design shall have individual feeders in separate segregated compartments, with proper barriers between adjacent feeders, bus bar chamber and cable termination chambers.

vii)	All feeders in compartmentalized design for housing ACB's or MCCB's shall have door interlocking such that the door cannot be opened with the switch in closed position.

viii)	All feeder terminations shall be properly terminated to receive Aluminum heavy duty power cables or 1.1 kV grade stranded copper cables as the case may be. Adequate space shall be provided to facilitate proper and easy terminations. Details of the same shall clearly be brought out in the layout and sectional views which the contractor is required to furnish.

(xix)    The feeder terminations shall be either from the top or bottom as necessary at site.

ix)	Wherever necessary, if the switch boards are to be mounted against a wall, the lay-out of the components and interconnections shall be designed to facilitate maintenance from the front.

x)	The design of the switch board shall be such that clear segregation shall be provided for the various components, feeders and interconnections - such as bus bars, incoming / outgoing feeders, cable chambers, etc. The height of the panel shall not exceed 2200 mm. The maximum   operating height of any components shall not exceed 1700 mm.

xi)	A minimum clearance of 25 mm between phases and between phases and neutral shall be maintained.

xii)	An Aluminum earth strip / bus of adequate section shall be run throughout the length of the switch board to which all earth terminals of the various components shall be connected.

(xiii) 	Bus bars shall be of Aluminum.

The bus bars shall have uniform cross section throughout and shall be capable of carrying. The rated current under the increased ambient temperature conditions within the enclosure. Unless otherwise specified, the neutral shall have a rating of 50 % of the phase bus bars. The bus bar sizes shall be specified in the drawings to be submitted by the contractor.

(xiv)	The Air circuit breakers, MCCB's, etc., shall have the features as specified in the bill of quantities.

- All MCCB's at SDB's and MCC's shall be of current limiting type with breaking capacity of min. 70 kA and with Ics = 100% leu

(xvi)	All control wiring shall be carried out with 1.1 kV grade single core PVC cables with stranded copper conductors of minimum 1.5 mm² for potential circuits, and 2.5 mm² for current transformer circuits. The wiring shall be neatly bunched, adequately supported and properly routed. The wires shall be identified by ferrules at both ends.

(xvii)	Terminal blocks shall be of 500 volts grade and with minimum current rating of 10 amps.

(xviii)	All routine tests as specified in the Indian Standards shall be carried out in the presence of TSSPDCL / Consultants and test certificates submitted for approval.

Test certificates shall also be submitted for all major components of the switch boards like    ACB's, CT's, Relays, etc.,

(xix)	Prior to fabrication of the panels, the contractor has to submit the following drawings for approval:

(a) Single line diagram

(b) Power circuit Control circuit diagrams

(c) Front view showing layout of components

(d) Sectional view

(e) Foundation drawings

(xx)	The outgoing cable feeders in distribution boards shall be either from top or bottom as necessitated at site conditions and this shall be properly examined prior to fabrication of boards.

2.2	The detailed specifications of the individual components have been furnished in the Bill of Quantities and only components of makes as recommended in the tender shall be provided.

2.3	All routine tests as per IS shall be conducted on the main distribution boards and sub distribution boards prior to dispatch / supply. The tests shall include all operational tests and shall also cover sequencing and interlocking functions wherever provided.

2.4	The following documents in 5 sets shall be furnished prior to dispatch / supply:

(i)  Routine test certificates of complete panels

(ii)  Routine test certificates for major components breakers, etc.,

(iii)All final drawings as listed in item 2.1(xviii)

(iv)Operation and maintenance manual for the panels

- 2.5	On completion of installation, necessary tests shall be performed at site prior to commissioning.

2.6    The scope of supply shall cover all installation materials such as base channels on which the switch board shall rest, foundation bolts, nuts, etc., & any	other installation materials as necessary.

2.7   All meters shall be of digital type and CT secondary shall be rated for 1 A.

3.0   MCB Distribution Boards.

3.1	Distribution boards shall be made of 1.6 mm thick sheet steel for body and 2 mm thick for doors powder coated with approved shade. The bus bar system shall be of integral single piece which is separated by SMC insulating material. The bus bars shall be of Copper electrolytic ally plated and rated for 200 A capacity. Separate neutral links and earth bus bar should be provided.

The boards shall conform to IS: 8623 standards & shall be factory built.

The bus bars shall be properly shrouded with 3 mm thick hylam sheets.

  - Body shall be connected to earth bus by green 4 sq mm copper flexible wires.

- 3.3	The MCB DB's shall be of industrial type with double door and intended for wall mounting. The DB's shall be of concealed type with its outer door flush with the wall. Both the inner and outer doors shall be of hinged type. The depth of DB's shall not exceed 125 mm.

The neutral bus and earth bus shall not foul with the leading in and out of the Aluminum /Copper cables and hence shall be separately located.

The neutral and earth bus shall preferably be at the top so that the neutral and earth core of outgoing feeders can be terminated very near the cable gland itself.

3.4     The DB's shall be dust and vermin proof and with degree of protection IP 54.

3.5      The DB's shall be complete--with internal wiring from the bus bars to the MCB terminals by means of 1.1 kV grade flexible copper cables of the following sizes.

for current up to 10 A		                    2.5 mm²

above l0A up to & including 20 A              4 mm²

above 20 A up to & including 30 A            6 mm²

3.6      Terminations shall be with insulated lugs crimped to the bus bars / MCB's.

3.7	Wherever Incoming feeders exceed 32 A, epoxy moulded bolted type ACDC make terminals shall be provided to which the Incoming cables can be terminated. Wiring from these terminals to Incoming MCB / MCCB termination shall be with flexible copper.

3.8    Cable gland plate detachable type shall be provided as required to suit site conditions.

3.9    The maker of DB's shall be as per the recommended list.

4.0   CONCEALED CONDUIT WIRING SYSTEM

4.1    CONDUIT LAYING

Conduits shall be laid on the finished centering with at least 3mm cover and this may be achieved by supporting the conduits on spacers kept at regular at regular intervals. Conduits shall be laid as far as possible straight runs.

Open ends of the conduits / junction boxes shall be well sealed with PVC caps to prevent entry of concrete slurry. The conduits and the junction boxes shall be tied to the reinforcement with binding wires at regular intervals to prevent them from getting dislodged while the concrete vibrator is applied for consolidating the concrete. PVC solution shall be applied for all conduit joints / connections.

4.2	DRAWING OF WIRES

Guidelines as stipulated in IS shall be followed and the contractor shall also obtain approval from the architects/ consultant prior to commencement of work.

4.3   BUNCHING OF CABLES

Cables carrying alternating current shall be so bunched that the outgoing & return cables are always drawn into the same conduit.

4.4    BENDS IN CONDUITS

All necessary bends in the system including diversion shall be done by bending pipes as far as possible or by inserting suitable inspection facilities. Radius of bends in conduit pipes shall not be less than 7.5 cm. No dent/crack shall be made on the pipes while bending.

4.5    FIXING OF CONDUIT IN CHASE

The conduit pipes shall be fixed by means of hooks or by means of saddles not more than 60 cm apart or by any other approved means of fixing. Fixing of standard bends or elbows shall be avoided as far as practicable and all curves maintained by bending the conduit pipe itself with a long radius which will permit easy drawing in of conductors.

4.6   FISH WIRE

To facilitate easy drawing of wires in the conduit suitable size steel wire shall be provided along with laying of conduit.

4.7   ERECTION AND EARTHING OF CONDUITS AND BOXES

The conduit of each circuit or section shall be laid and inspected before conductors are drawn in. If conduit pipes are liable to mechanical damage, they shall be adequately protected. In conduit wiring system the pipe must be continuous when passing through walls of floors. All metal boxes shall be effectively earthed.

4.8   TERMINATION OF CONDUITS

Wherever conduits are terminated in an outlet box or a distribution board, flexible pipes with check nuts shall be fixed on either side of the box. After the conduits, junction boxes, outlets boxes, etc., are fixed in position and wires are drawn, their outlets shall be properly plugged using PVC stopper or rubber bushing to prevent entry of mortar, vermin's or any other foreign material into the conduit system.

4.9 	Separate conduit wiring for 100W 4 No’s shall be provided for separate DC wiring in the control room.

SECTION 6

QUALITY ASSURANCE PLAN

QUALITY ASSURANCE PROGRAMME

1.	To ensure that the equipments are in accordance with the specifications, the contractor shall adopt suitable quality assurance programme to control such activities at all points, as necessary. Such programme shall be out lined by the contractor and shall be finally accepted by owner/ authorized representative after discussions before the award of contract. The QA programme shall be generally in line with ISO-9000/IS-14000. A quality assurance programme of the contractor shall generally cover the following:

i)	His organization structure for the management and implementation of the proposed quality assurance programme.

ii)	Quality system manual.

iii)	Design control system.

iv)	Documentation control system

v)	Qualification data for bidder’s key personnel.

vi)	The procedure for purchase of material, parts, components and selection of sub vendors service including vendor analysis, source inspection, incoming raw material inspection, verification of materials purchased etc.,

vii)	System for shop manufacturing control including process controls, fabrication and assembly controls.

viii)	Control of non conforming items and systems for corrective actions.

ix)	Inspection and test procedure as per relevant ISS.

x)	Control of calibration and testing of measuring and testing equipment as per standards.

xi)	System for indication and appraisal of inspection status.

xii)	System for quality audit

xiii)	System for authorizing release of manufactured product to owner.

xiv)	System for maintenance of records

xv)	System for handling storage and delivery

xvi)	All the plant standard/ written down practices followed by the manufacturer/ contractor against the manufacturing activities in their works will be submitted in electronic media preferably in at least one set of compact discs.

2.	GENERAL REQUIREMENTS – QUALITY ASSURANCE PLAN

2.1	All materials, components and equipment covered under this specification shall be procedure manufactured and tested at all the stages, as per a comprehensive quality programme. An indicative programme of inspection/ tests to be carried out by the contractor for some of the major items is given in this specification. This is however, not intended to form a comprehensive programme as it is the contractor’s responsibility to draw up and implement such programme duly approved by the Owner. The detailed quality plans for the manufacturing activities should be drawn up by the bidder, and will be submitted to Owner for approval. Schedule for finalization of such quality plans will be finalized before award.

2.2	Manufacturing quality plan shall detail out for all the components and equipments, various tests, inspection, to be carried out as per the requirements to this specification and standards mentioned therein and quality practices and procedures followed by contractor’s Quality Control Organization, the relevant reference documents and standards acceptance norms, inspection documents raised etc., during all stages of material procurement, manufacture, assembly and final testing/ performance testing.

2.3	The bidder shall also furnish copies of the reference documents/ plant standard / acceptance norms/ test and inspection procedure etc., as referred in Quality Plan along with Quality Plans.

2.4	The Quality Plans and reference documents/ standards etc., will be subject to Owner’s approval and will form a part of the contract. In these approved Quality Plan, Owner shall identify customer hold points (CHP) which shall be carried out in presence of the Owner’s Project Manager and beyond which work shall not proceed without, written consent of Owner’s Project Manager/ authorized representative in writing. All deviation to this specifications, approved quality plans and applicable standard must be documented and referred to Owner along with technical justification for approval and dispositioning.

2.5	No material shall be dispatched from the manufacture’s works before the same is accepted subsequent to pre-dispatch final inspection including verification of records of all previous tests/ inspections by Owner’s Project Manager/ authorized representative, and duly authorized for dispatch issuance of MDCC.

2.6	All materials used and supplied shall be accompanied by valid and approved materials certificates and tests and inspection reports. These certificates and reports shall indicate the heat numbers or other such acceptance identical numbers of the material. The material certified shall also have the identification details stamped on it.

2.7	All materials used for equipment manufacture including casting and forging etc. shall be of tested quality as per relevant codes/ standard. Details of results of the tests conducted to determine the mechanical properties, chemical analysis and details of heat treatment procedure recommended and actually followed shall be recorded on certificates and time temperature chart. Tests shall be carried out as per applicable material standards and / or agreed details.

2.8	All welding and brazing shall be carried out as per procedure drawn and qualified in accordance with requirements of ASME section-IX/ BS-4870 or other international equivalent standard acceptance to the Owner.

2.9	All welding/ brazing procedure shall be submitted to the Owner or its authorized representative for approval prior to carrying out the welding/ brazing.

2.10	All brazers, welders and welding operators, employed on any part of the contract either in contract / his sub-contractors works or at site elsewhere shall be qualified as per ASME section-IX or BS-4871 or other equivalent International Standards acceptable to the Owner.

2.11	Test results of qualification tests and specimen testing shall be furnished to the Owner for approval. However where required by the Owner, tests shall be conducted in presence of Owner/ authorized representative.

2.12	All the heat treatment results shall be recorded on time temperature charts and verified with recommended regimes.

2.13	Results of all non-destructive testing shall be recorded on certificates.

2.14	All the sub-vendors proposed by the contractor for procurement of major bought out item including castings, forgings, semi-finalized and finished components/ equipment, list of which shall be drawn up by the contractor and finalized with the Owner shall be subject to Owner’s approval. The contractor’s proposal shall include vendor’s facilities established at the respective works, the process capability, process stabilization, QC Systems followed, experience list etc. along with his own technical evaluation and shall be submitted to the Owner for approval prior to any procurement. Such vendor approval shall not relieve the contractor from any obligation, duty or responsibility under the contract.

2.15	For components/ equipment procured by the contractors for the contract, after obtaining the written approval of the Owner, the contractor’s purchase specifications and enquiries shall call for quality plans to be submitted by the suppliers along with their proposals. The quality plans called for from the vendors shall set out, during the various stages of manufacture, the quality practices and procedures followed by the vendor’s quality control organization, the relevant reference documents/ standards used, acceptance level, inspection of documentation raised etc.,

2.16	Such quality plans of the successful vendors shall be finalized with the Owner and such approved quality plans shall form a part of the purchase order/ contracts between the contractor and the vendor, within three weeks of the release of the purchase order/ contract for such bought out items/ components, a copy of the same without price details but together with the detailed purchase specifications, quality plans and delivery conditions shall be furnished to the Owner by the contractor.

2.17	The purchase specifications for the major bought out items, list of which shall be drawn up by the contractor and finalized with the Owner shall be furnished to the Owner for comments and subsequent approval before orders are placed.

2.18	Owner reserves the right to carry out quality audit and quality surveillance of the systems and procedures of the contractor’s or their sub-vendor’s quality management and control activities. The contractor shall provide all necessary assistance to enable the Owner carry out such audit and surveillance.

2.19	The contractor shall carry out an inspection and testing programme.

2.20	Quality audit/ surveillance/ approval of the results of the tests and inspection will not, however, prejudice the right of the Owner to reject the equipment if it does not comply with specification when installed or does not comply with the specification in service and the above shall in no way limit the liabilities and responsibilities of the contractor in ensuring complete conformance of the materials/ equipment supplied to relevant specification, standard, data sheet, drawings etc.,

2.21	For all spares and replacement items, the quality requirements as agreed for the main       equipment supply shall be applicable.

2.22	Repair/ rectification procedures to be adopted to make the job acceptable shall be subject to the approval of the Owner/ authorized representative.

3.	QUALITY ASSURANCE DOCUMENTS

3.1	The contractor shall be required to submit two sets of compact discs of the following Quality Assurance Documents within three weeks after dispatch of the equipment.

i)	The inspection plan with verification, inspection plan check points, verification sketches, if used and methods used to verify that the inspection and testing points in the inspection plan were performed satisfactorily.

ii)	Factory tests results for testing required as per applicable codes and standard referred in the specification.

iii)	Inspection reports duly signed by QA personnel of the Owner and contractor for the agreed inspection hold points. During the course of inspection, the following will also be recorded.

- When some important repair work is involved to make the job acceptable; and

- The repair work remains part of the accepted product quality.

iv)	All the accepted deviations shall be included with complete technical details.

SECTION – 7

SCHEDULE OF QUANTITIES AND PRICES

- PREAMBLE

- The schedule of Quantities shall be read in conjunction with the Instructions to Bidders. General and Special Conditions of Contract, Technical Specifications and Drawings and schedule-A of price bid document where quantities and their estimated values are mentioned.

- The quantities given are estimated and provisional, and are given to provide a common basis for bidding.  The basis of payment will be the actual quantities of work ordered and carried out, as measured by the Contractor and verified by the Engineer and valued at the rates and prices tendered in the schedule-A of price bid document. Where applicable and otherwise at such rates and prices the Engineer may fix within the terms of the Contract.

- The rates and prices tendered in the schedule-A of price bid document shall, except in so far as it is otherwise provided under the Contract, include all constructional plant, labour, supervision materials, erection maintenance, insurance, profit. Taxes and duties, together with all general risks, liabilities and obligations set out or implied in the contract.

- The whole cost of complying with provisions of the Contract shall be included in the items provided in the schedule-A of price bid document, and where no items are provided the cost shall be deemed to be distributed among the rates and prices entered for the related items of work.

- General directions and descriptions of work and materials are not necessarily repeated nor summarized in the schedule-A of price bid document. References to the relevant sections of the contract documentation shall be made before entering prices against each item in the price schedule of Quantities.

- The method of measurement of completed work which means supply erection and fixing of cross arms and other necessary auxiliaries in case of PSCC poles and the payment shall be in accordance with relevant I.S.S. Codes.

- The method of measurement of completed work of payment shall be in accordance with relevant I.S.S. Codes.

- Rock defined as all materials which, in the opinion of the Engineer require blasting or the use of metal wedges and sledge hammers or the use of compressed air drilling for its removal and which cannot be extracted by ripping with tractor at least with 150 BHP with single rear mounted heavy duty ripper.

BID No. Chief General Manager/Master Plan /GH/TSSPDCL:  06-A/2022-23

| SCHEDULE OF QUANTITIES AND PRICES S. No. | Name of the Substation | Name of the Mandal | Compound wall Civil work cost in Rs |
| --- | --- | --- | --- |
| 1 | Compound wall -Uppal Bhagayat Phase-II | Uppal | Rs.21,11,781.37 /- |

| RCC (Cu.m) | Steel(MT) | Brick Masonry (Cu.m) | Plastering (sqm) |
| --- | --- | --- | --- |
| 37.41 Cu.m | 3.367 MT | 54.03 Cu.m | 643.36 sqm |

Total cost of the Bid is Rs. 21,11,781.37 /- (Rupees Twenty One Lakhs Eleven Thousand Seven Hundred Eighty One and Paise Thirty Seven Only) exclusive of service tax.

(All the item wise rates are exclusive of GST.)

Further, vide Memo No. CGM(Fin)/ GM(SP&Trust) /AAO(SP) /D.No.161/2022,   Dt.27.10.2022, instructions have been received from the CGM/Finance/TSSPDCL to recover @0.01% from all the works contract for Haritha Nidhi (Telangana Green Fund).

SECTION - 8

SAFETY MEASURES

The Contractor shall maintain safety tools and materials as per the work to be carried out.

TSSPDCL is not liable for any accident or untoward incident during the execution of work.

Warnings Signs

Different types of warning signs such as "Men working", "Line under permit to work", "Danger", etc and other indications for earthing, live parts, shock hazard possibility etc are to be displayed at strategic points by the contractor.

The contractor shall utilize the safety material as detailed during the execution of work.

Rubber Gloves

These are specially processed gloves, high dielectric strength, hardened as required and with flexibility for normal bend of fingers and thumbs for operating equipment handles.

Work Gloves

These are gloves made of silicon grain leather, flexible and with large protective cuff. These gloves are used while working on equipment for pre-commissioning tests or for repairs.

Polyethylene helmets

Safety hats for industrial and construction use, with tough outer shell, brims to allow water to drain and with adjustable side ventilation, in standard sizes.

Insulated boots

These are boots made of special leather with elastomeric canvas support, flexible with anti-slip sole.

Safety Unit

Safety clothing, include safety suit with no metal parts, resistant to wear and tear, flexible comfortable with Velcro straps.

Hooded Rain Coat

PVC rain garment with matching nylon trousers for the use of workmen during rains.

Reinforced Safety Belt

These are waist belts for use in the overhead line work, with polyamide or leather elements, cast steel buckles suspension rings, straps, fiber ropes etc. Anti-fall safety-snaps will also be part of the safety belt.

Portable lamps’

In the safety tools of workmen, head lamps, pocket torch, hand lamps etc are also included.

Life saving Kits

These shall contain, voltage detectors, cable cutter with insulated handles and insulated platform on ladder and rescue sticks.

Fire Extinguisher -

Normally CO2 cylinder 4.5'*g, 6.5 kg, 9 kg, 22 kg are used in sub-stations and generating stations. 22 kg cylinders are generally trolley mounted type.

The work area shall be separated from all possible sources of supply of power, by ensuring relevant circuit breakers, isolating switches etc.

The equipment like breakers and isolators shall be locked in the open condition.

- Warning boards shall be exhibited even during the simple temporary maintenance       operation,

- The area of work shall be properly demarcated with identifying ribbons or ropes.

- Each conductor or apparatus shall be checked to ensure absence of voltage.

- Proper short circuit and earthing shall be made before commencing any work on the line or equipment.

All safety rules given above and other associated guide lines are for enhancing safety when a person is in contact with or in close proximity to an electrical network. Using proper ladders, safety belts, helmets, insulating gloves etc form part of the safety rules, as observation of the same are essential for preventing accidents other than the electrical shock hazard.

Safety Checks

The safety checks include the following

- Whether the worker is properly trained for the work and aware of safety rules?

ii)  Whether appropriate tools, and gadget available for the work? AN%

iii) Whether the' person is properly insulated by using insulated platform, gloves, mats etc.?

iv) Whether the active or live conductors are away at a safe distance?

v)   Whether safety equipment like helmets, safety belts, fire fighting equipment, earth rods etc. available?

vi) Whether all accidental reconnection of supply or induced voltage possibilities are guarded against?

vii) Whether life saving kits and first aid equipment available?

Safety Measures during erection of lines and installation of Equipment 3.5.1 Excavation for Foundations.

• The excavation for pad or pile type foundations in excess of 1.5 meters depth located on unstable earth shall be either sloped to the angle of repose or shored if entry is required., Ladders shall be used for access to pad or pile type footing excavations in excess of 1.2 meters.

Workmen shall not enter excavated pit in un-stable earth unless shoring is used to protect them.

- Workmen shall not remain in the excavated pit where concreting is done using machinery.

- Mobile machines for concreting shall be located only on leveled earth to ensure stability.

SECTION - 9

FORM OF BID, QUALIFICATION INFORMATION, PERFORMANCE BANK GUARANTEE AND LETTER OF ACCEPTANCE

TABLE OF FORMS:

- CONTRACTOR’S BID

- QUALIFICATION INFORMATION

- LETTER OF ACCEPTANCE

- NOTICE TO PROCEED WITH THE WORK

- BID SECURITY BANK GUARANTEE

- PERFORMANCE SECURITY BANK GUARANTEE

- AGREEMENT FORM

- DECLARATION FORM

CONTRACTOR’S BID

Description of the Works ______________________________________________________________________________________________________________________________________________________________________________________________

BID

To	:  Chief General Manager /Master Plan, TSSPDCL, Mint Compound, Hyderabad-500063.

(The Employer)

Gentlemen,

We offer to execute the Works described above in accordance with the Conditions of Contract accompanying this Bid for the Contract Price of ____________ (in figures) (________________________________________________) in letters.

Whether advance is available or not the advance payments required is: Rupees_________________

This Bid and your written acceptance of it shall constitute a binding contract between us.  We understand that you are not bound to accept the lowest or any Bid you receive.

Commission or gratuities, if any, paid or to be paid by us to agents relating to this Bid, and to contract execution if we are awarded the contract, are listed below:

Name and address of agent		Amount	Purpose of Commission on gratuity/

……………………………….		…………..	………………………………………..

……………………………….		…………..	………………………………………..

……………………………….		…………..

(If none, state “none”)

We hereby confirm that this Bid complies with the Bid Validity and Bid Security required by the Bidding documents.

We attach herewith our current income-tax clearance certificate.

Yours faithfully,

Authorized Signature:

Name & Title of Signatory: _______________________________________________

Name of Bidder: _________________________________________________

Address: __________________________________________________

  - To be filled by Bidder, together with his particulars and date of submission at the bottom of the form of Bid.

QUALIFICATION INFORMATION

The information to be filled in by the Bidder in the following pages will be used for purposes of post – qualification as provided for in Clause 4 of the instructions to Bidders.  This information will not be incorporated in the Contract.

- For Individual Bidders

  - Constitution or legal status of Bidder

(Attach Copy)

Place of Registration:

Principal place of business:

Power of Attorney of Signatory of Bid

(Attach)

  - Total value of Electrical Engineering Construction

  - Work performed in the last five years.

(in Rs. Crores)

    - Work performed as prime contractor (in the same name) on works of a similar nature over the last five years duly furnishing date of charging & date of issue of performance certificate (or) to specify the period of satisfactory performance in the performance certificates

| Project Name | Name of Employer | Description of work | Contract No. | Value of contract (Rs. Cores) | Date of issue of work order | Stipulated period of completion | Actual date of commencement, completion and charging, date of issue of performance certificate | Remarks Explaining reasons for delay and work completed |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Note: 	The certificates shall be attested by not less than the Divisional Engineer, Construction in Charge of the work.

    - Quantities of work executed as prime contractor (in the same name and style) in the last five years.

Year		Name of the work  		             Qty	      Amount in Rs. Lakhs

1. Erection of 33/11kV substations Indoor or outdoor

2. Erection of length of new Line/UG Cable (route length)

(33kV & 11kV)

- Enclose certificate(s) from the Engineer(s) in-charge.

@ The item of work for which data is requested should tally with that specified in ITB clause 4.3.

**   Immediately preceding the financial year in which bids are received.

  - Information on Bid Capacity (works for which bids have been submitted and works which are yet to be completed) as on the date of this bid.

- Existing commitments and on-going works in MasterPlan zone and other works.

| Description of work | Place & State | Contract No. & Date | Name and Address of employer | Value of Contract (Rs. Crores) | Stipulated period of completion | Value of works remaining to be completed Rs. Crores | Anticipated date of completion |
| --- | --- | --- | --- | --- | --- | --- | --- |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) |

- Works for which bids already submitted:

| Description Of Work | Place & State | Estimated value of works (Rs. Lakhs) | Stipulated period of completion | Date when decision is expected | Remarks if any |
| --- | --- | --- | --- | --- | --- |
| (1) | (2) | (3) | (4) | (5) | (6) |

- Enclose certificate (s) from the Engineer (s)-in-Charge.

  - The following items of Contractor’s Equipment are essential for carrying out the Works.

The Bidder should list all the information requested below.  Refer also to Sub Clause 4.3 of the Instructions of Bidders. Declaration for rollers and cable laying works should invariably be included along with all the other relevant equipments.

| Item of equipment | Requirement No. Capacity | Availability proposals Owned/leased/ to be procured | Nos./ capacity | Age/ condition | Remarks (from whom to be purchased) |
| --- | --- | --- | --- | --- | --- |

  - Qualifications and experience of key personnel proposed for administration and execution of the Contract, Attach biographical data.  Refer also to Sub Clause 4.3of instructions to Bidders and Sub Clause 9.1 of the Conditions of Contract. Educational certificates must be submitted.

| Position Project Manager Etc. | Name | Qualification | Years of experience (general) | Years of experience in the proposed position |
| --- | --- | --- | --- | --- |

  - Financial reports for the last five financial years: Turnover balance sheets, profit and loss statements, Income tax return statements, auditors reports (in case of companies/corporation) etc.  List them below and attach copies.

  - Evidence of access to financial resources to meet the qualification requirements: cash in hand, lines of credit, etc.  List them below and attach copies of support documents.

1.9 Name, address and telephone, telex, and fax numbers of the Bidders’ bankers who may provide references if contacted by the Employer.

  - Performance certificate for the works executed is to be furnished

  - Statement of compliance under the requirements of Sub Clause 3.2 of the instructions to Bidders.

1.12 Proposed work method and schedule.  The Bidder should attach descriptions, drawings and charts as necessary to comply with the requirements of the Bidding documents.  (Refer ITB Clause 4.1 and 4.3.

- Additional Requirements

Bidders should provide any additional information required to fulfill the requirements of Clause 4 of the instructions to the Bidders, if applicable.

ANNEXURE – I

Declaration to be given by the Company/ Partnership Firm/ Contractor at the time of entering into agreement with TRANSCO/ DISCOMs.

I, _______________________________________________________ representing the Company / Partnership Firm/ Contractor responding to the bid invitation by the TRANSCO/ APEPDCL/ APSPDCL/ TSNPDCL/ TSSPDCL vide Specification No. _____________________ hereby sincerely and solemnly affirm and state as follows:

(Strike out that which is not applicable)

a)	That myself or any of the representatives of my company/ firm do not have any relatives as defined in the appended Annexure-III in the TRANSCO/ DISCOM.

(Or)

b)	That the following officers/ employees of the TRANSCO/ DISCOM are related to me and to the representatives of my company / firm and their status in the TRANSCO/ DISCOMs is as under.

| S.No. | Name of the officer/ employee | Designation and place of working | TRANSCO/ DISCOM | Relationship |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |

It is certified that the information furnished above is true to the best of my knowledge and belief. It is hereby undertaken that in the event of the above information found to be false or incorrect at a later date, the TRANSCO/ DISCOM is entitled to terminate the contract/ agreement entered into besides recovering damages as may be found necessary, with due notice.

Signature of the authorized representative

ANNEXURE – II

Declaration to be given by the Company/ Partnership Firm/ Contractor at the time of entering into agreement with TRANSCO/ DISCOMs.

(Strike out that which is not applicable)

a)	I declare that myself or any of the representatives of my company/ firm do not have any relatives as defined in the appended Annexure-III in the TRANSCO/ DISCOM.

(or)

b)	That the following officers/ employees of the TRANSCO/ DISCOM are related to me and to the representatives of my company / firm as mentioned here under.

| S.No. | Name of the officer/ employee | Designation and place of working | TRANSCO/ DISCOM | Relationship |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |

It is certified that the information furnished above is true to the best of my knowledge and belief. It is hereby undertaken that in the event of the above information found to be false at a later date, the TRANSCO/ DISCOM is entitled to terminate the contract/ agreement entered into besides recovering damages as may be found necessary, with due notice.

Signature of the authorized representative

ANNEXURE – III

List of Relatives:

1)	Father					14)	Daughter’s Husband

2)	Mother (including Step Mother)	15)	 Daughter’s Son

3)	Son (including Step Son)		16)	Daughter’s Son’s Wife

4)	Son’s wife				17)	Daughter’s Daughter

5)	Daughter (including Step Daughter)	18)	Daughter’s, Daughter’s Husband

6)	Father’s Mother			19)	Brother (including Step Brother)

7)	Father’s Father			20)	Brother’s Wife

8)	Mother’s Father			21)	Sister (including Step Sister)

9)	Mother’s Mother			22)	Sister’s Husband

10)	Son’s Son 				23)	Son’s Wife’s Father 	and

their

11)	Son’s, Son’s Wife			24)	Son’s Wife’s Mother	siblings

12)	Son’s Daughter  			25)	Daughter’s Husband’s Father

and their siblings

13)	Son’s Daughter’s Husband		26)	Daughter’s Husband’s Mother

LETTER OF INTENT

(Letterhead paper of the Employer)

____________________ (date)

To:

___________________________________________   (Name and address of the Contractor)

Dear Sirs,

This is to notify you that your Bid dated_________for execution of the_________

_______________________________________________________________ (name of the contract and identification number, as given in the instructions to Bidders)1 for the  Contract Price of Rupees__________________________________________________

___________________________________ _(__________________) (Amount in words and

Figures), as corrected and modified in accordance with the instructions to Bidders’ is hereby accepted by our Agency.

You are hereby requested to furnish Performance Security, plus additional security for unbalanced bids in terms of ITB clause 27.4 in the form detailed in Para 31.1 or ITB for an amount of Rs.____________ within 21 days of the receipt of this letter of acceptance valid up-to 28 days from the date of expiry of Defects Liability Period i.e. up-to ……………… and sign the contract, failing which action as stated in Para 31.3 of ITB will be taken.

Yours faithfully,

Authorized Signature

Name and Title of Signatory

Name of Agency

Chief General Manager/ Master Plan

Southern Power Distribution Company of Telangana Limited,

Mint Compound,

Hyderabad -500063

1.	Delete “correct and” or “and modified” if only one of these actions applies.  Delete “as corrected and modified in accordance with the Instructions to Bidders” if corrections or modifications have been effected.

2	To be used only if the Contractor disagrees in his Bid with the Technical Expert proposed by the Employer in the “Instructions to Bidders”.

ISSUE OF NOTICE TO PROCEED WITH THE WORK

(Letterhead of the Employer)

____________ (date)

To

_____________________(Name and Address of the Contractor)

Dear Sirs,

Pursuant to your furnishing the requisite security as stipulated in ITB clause 31.1 and signing of the contract for the construction of -------------------------@ a Bid price of Rs. ------------------------, you are hereby instructed to proceed with the execution of the said works in accordance with the contract documents.

Yours faithfully,

Chief General Manager/ MasterPlan

Southern Power Distribution Company of Telangana Limited

(Signature, name and title of signatory

Authorized to sign on behalf of Employer)

BANK GUARANTEE FOR 2% BID SECURITY

To

The Chief General Manager/Master Plan

TSSPDCL, Mint Compound, Hyderabad.

Whereas.............. (hereinafter called "the Bidder") has submitted its Bid dated (date of    submission of bid) for the work   ....................(name and /or description of the work) (hereinafter called "the Bid").

KNOW ALL PEOPLE by these presents that WE.  ............. (name of bank) having our registered office at.  ........... (address of bank)(hereinafter called "the Bank"), are bound unto you,  in the sum of Rs. ………..     for which payment well and truly to be made to you, the Bank binds itself, its successors, and assigns by these presents. Sealed with the Common Seal of the said Bank this          day of             2019.

THE CONDITIONS of this obligation are:

1.	If the Bidder

a) withdraws its Bid during the period of bid validity specified by the Bidder on the Bid Form; or

b) does not accept the correction of errors in accordance with the Bid Specification, or

2.	If the Bidder, having been notified of the acceptance of its bid by you, during the period of bid validity;

(a)	fails or refuses to furnish the performance security, in accordance with the Bid Specification.

(b) fails or refuses to execute the Contract Form if required; or

We undertake to pay you up to the above amount upon receipt of its first written demand, without having to substantiate its demand, provided that in its demand you will note that the amount claimed is due to it, owing to the occurrence of one or both of the two conditions, specifying the occurred condition or conditions.

This guarantee will remain in force up to 6 months from the uploading starting date of the Bid …………….(Specification Date) and any demand in respect thereof should reach the Bank not later than the above date.

.  ....................

(Signature of the Bank)

NOTE:	This will be executed on a Rs.100/- non-judicial stamp paper issued by any Nationalized/Scheduled Bank.

PERFORMANCE BANK GUARANTEE

To

The Chief General Manager/Master Plan

TSSPDCL, Mint Compound, Hyderabad.

Whereas __________________________________________ [name and address of Contractor]

(hereinafter called “the Contractor”) has undertaken, in pursuance of Contract No. _______________dated _______________ to execute _______________ [name of Contract and brief description of Works] (hereinafter called “the Contract”).

AND WHEREAS it has been stipulated by you in the said Contract that the Contractor shall furnish you with a Bank Guarantee by a recognized bank for the sum specified therein as security for compliance with his obligations in accordance with the Contract “

AND WHEREAS we have agreed to give the Contractor such a Bank Guarantee:

NOW THEREFORE we hereby affirm that we are the Guarantor and responsible to you, on behalf of the Contractor, up to a total of ___________________ [amount of guarantee]* ____________________ [in words], such sum being payable in the types and proportions of currencies in which the Contract Price is payable, and we undertake to pay you, upon your first written demand and; without cavel or argument, any sum or; sums within the limits of ___________________ [amount of guarantee]* as aforesaid without your needing to prove or to show grounds or reasons for your demand for the sum specified therein.

We hereby waive the necessity of your demanding the said debt from the Contractor before presenting us with the demand.

We further agree that no change or addition to or other modification of the terms of the Contract or of the Works to be performed there under or of the Contract documents which may be made between you and the Contract shall in any way release us from any liability under this guarantee, and we hereby waive notice of any such change, addition or modification.

This guarantee shall be valid until 28 days from the date of expiry of defects liability period of the said contract.

Signature and seal of the Guarantor ______________________

Name of Bank _______________________________________

Address _______________________

Date ____________________________

*An amount shall be inserted by the Guarantor, representing the percentage of the Contract Price specified in the Contract including additional security for unbalanced Bids, if any and denominated in Indian Rupees

AGREEMENT FORM

This agreement, made the -------------------------day of --------------- Year --------between

--------------------------------------------------(Name and Address of Employer).

(Hereinafter called “the Employer)” and------------------------------------------------------------

-----------------------------------------------[Name and Address of Contractor] (hereinafter called “the Contractor” of the other part).

Whereas the Employer is desirous that the Contractor execute----------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------)

Name and identification number of Contract] (hereinafter called “the Works’) and the Employer has accepted the Bid by the Contractor for the execution and completion of such Works and the remedying of any defects therein, at a cost of Rs………………….

NOW THIS AGREEMENT WITNESS as follows:

1.	In this Agreement, words and expression shall have the same meanings as are respectively assigned to them in the Conditions of contract hereinafter referred to, and they shall be deemed to form and be read and construed as part of this Agreement.

2.	In consideration of the payments to be made by the Employer to the Contractor as hereinafter mentioned, the Contractor hereby covenants with the Employer to execute and complete the Works and remedy and defects therein conformity in all aspects with the provisions of the Contracts.

3.	The Employer hereby covenants to pay the Contractor in consideration of the execution and completion of the Works and the remedying the defects wherein the Contract price or such other sums as may become payable under the provisions of the Contract at the times and in the manner prescribed by the Contract.

4.	The following documents shall be deemed to form and be read and construed as part of this Agreement, viz.:

Letter of Acceptance;

Notice to proceed with the works;

Contractor’s Bid;

Contract Data;

Conditions of Contract;

Specifications;

Drawings;

Quality assurance plan; and

Any other document listed in the Contract Data as forming part of the Contract.

In witness where of the parties there to have caused this Agreement to be executed the day and years first before written.

The Common Seal of --------------------------------------------------------

Was hereunto affixed in the presence of:

Signed, Sealed and delivered by the said---------------------------------------------------------

In the presence of:

Binding Signature of Employer	---------------------------------------------------------------

Binding Signature of Contractor	---------------------------------------------------------------